## Sheet1
Monitoring of STPs as on 08.09.2026
[13 empty] | Outlet of STP | [60 empty] | Inlet of STP | [59 empty] | Analysis of STP Sludge Parameters
Sr. No. | STP's Name |  | BOD | pH | COD | TSS | O &G | Total Nitrogen | Total Phosphorous | F.Coli. | Collection Date | Report No. & date | Flow Outlet | PH (5.5 to 9.0) | BOD mg/l (10) | COD mg/l (50) | FOG (mg/l) | TSS mg/l (20) | TDS (mg/l) | Chloride (mg/l) | HCO3 (mg/l) | Sulphate (mg/l) | Fluoride (mg/l) | Total Nitrogen (mg/l) (10) | Amonical Nitrogen (mg/l) | Nitrate Nitrogen (mg/l) | Total Phosphorus (mg/l) (1) | Phosphate P (Dissolved ) (mg/l) | Total S (Sulphide) (mg/l) | Phenolic Compound (mg/l) | Sodium (mg/l) | Magnesium( mg/l) | Calcium (mg/l) | Ionic Detergents (MBAS) (mg/l) | Residual chlorine (mg/l) | Total Alkalinity as CaCo3 (mg/l) | Total Hardness (mg/l) | Fecal Coliform MPN/100 ml (<100) | E. Coli (MPN/ 100 ml) | Intestinal Helminth eggs (MPN/ 100ml) | Sodium Adsorption Ratio ( SAR) (meq/l) | Residual Sodium Carbonate (RSC) (meq/l) | Electrical Conductivity (EC) (umhos/cm) | Boron (mg/l) | Cu (Copper) (mg/l) | Fe (Iron) (mg/l) | Mn (Magnese) ( mg/l) | Cr (Chromium) (mg/l) | Ni (Nicke) (mg/l) | Pb (Lead) (mg/l) | As (Arsenic) (mg/l) | Cd (Cadmium) (mg/l) | Co (Cobalt) (mg/l) | Li (Lithium) (mg/l) | Zn (Zinc) (mg/l) | Hg (Mercury) (mg/l) | AI (Aluminium) (mg/l) | Be (Berylium ) ( mg/l) | CN (Cyanide) (mg/l) | Mo (Molybdenum) (mg/l) | Se (Selenium ) (mg/l) | V (Vanadium) (mg/l) | Ba (Barium) (mg/l) | Ag (Silver) (mg/l) | Oil & Grease mg/l (10) | Fecal Streptococci MPN/100ml | Total Coliform MPN/100ml | Conductivity us/cm | Total Kjeldahl Nitrogen (mg/l) | Total Phosphate (mg/l) | Nitrate (mg/l) | Remarks (actual/ legally) | Remarks | Flow Inlet | PH | BOD (mg/l) | COD (mg/l) | FOG (mg/l) | TSS (mg/l) | TDS (mg/l) | Chloride (mg/l) | HCO3 (mg/l) | Sulphate (mg/l) | Fluoride (mg/l) | Total Nitrogen (mg/l) | Amonical Nitrogen (mg/l) | Nitrate Nitrogen (mg/l) | Total Phosphorus (mg/l) | Phosphate P (Dissolved ) (mg/l) | Total S (Sulphide) (mg/l) | Phenolic Compound (mg/l) | Sodium (mg/l) | Magnesium (mg/l) | Calcium (mg/l) | Ionic Detergents (MBAS) (mg/l) | Residual chlorine (mg/l) | Total Alkalinity as CaCo3 (mg/l) | Total Hardness (mg/l) | Fecal Coliform MPN/100ml | E. Coli (MPN/ 100 ml) | Intestinal Helminth eggs (MPN/ 100ml) | Sodium Adsorption Ratio ( SAR) (meq/l) | Residual Sodium Carbonate (RSC) (meq/l) | Electrical Conductivity (EC) (umhos/cm) | Boron (mg/l) | Cu (Copper) (mg/l) | Fe (Iron) (mg/l) | Mn (Magnese) ( mg/l) | Cr (Chromium) (mg/l) | Ni (Nicke) (mg/l) | Pb (Lead) (mg/l) | As (Arsenic) (mg/l) | Cd (Cadmium) (mg/l) | Co (Cobalt) (mg/l) | Li (Lithium) (mg/l) | Zn (Zinc) (mg/l) | Hg (Mercury) (mg/l) | AI (Aluminium) (mg/l) | Be (Berylium ) ( mg/l) | CN (Cyanide) (mg/l) | Mo (Molybdenum) (mg/l) | Se (Selenium ) (mg/l) | V (Vanadium) (mg/l) | Ba (Barium) (mg/l) | Ag (Silver) (mg/l) | Oil & Grease | Fecal Streptococci MPN/100ml | Total Coliform MPN/100ml | Conductivity us/cm | Total Kjeldahl Nitrogen (mg/l) | Total Phosphate (mg/l) | Nitrate (mg/l) | Bypass | Collection date of sludge | Report No. & date | pH (6.5.7.5) | Conductivity Micro S/cm (4.0) | Arsenic mg/ Kg (10.0) | Lead mg/ Kg (100.0) | Mercury (mg/ Kg) (0.15) | Copper mg/kg (300.0) | Zinc mg/kg (1000.0) | Nickel mg/kg (50.0) | Iron mg/kg | Total Chromium mg/kg (50.0) | Hexavalent Chromium mg/kg | Cadmium mg/kg (5.0) | Total Nitrogen mg/kg minimum (0.8) | Total Phosphate mg/ kg minimum (0.4) | Total Potassium mg/ Kg minimum (0.4) | Total Organic Carbon % minimum (12.0) | Cobalt | Parameter not analysed (sludge)
[14 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | [6 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
Yamuna Catchment
Yamuna Nagar
1 | (YMN-STP-001) 25 MLD STP Radaur Road, Yamuna Nagar by PHED in 2001 (SBR) |  | 10 | 5.5 to 9 | 50 | 10
[11 empty] | 09.01.2026 | 4283 dt. 21.01.2026 |  | 1: 7.19; 2: 5.8; 3: 44; 5: 12; 11: ND |  |  |  | Complying | Complying
[11 empty] | 17.02.2026 | 4542 dt. 02.03.2026 | 740 | 1: 7.45; 2: 7.2; 3: 36; 5: 12; 11: ND; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 17.03.2026 | 4727 dt.01.04.2026 | 730 | 1: 8.23; 2: 3.6; 3: 24; 5: 18; 11: ND; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 09.04.2026 | 99 dt. 28.04.2026 | 8378 | 1: 8.16; 2: 7.5; 3: 44; 5: 12; 11: ND; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 19.05.2026 | 287 dt. 01.06.2026 |  | 1: 7.76; 2: 12; 3: 98; 5: 22; 11: 11.342; 25: 200 |  |  |  | Non-Complying | Non-Complying
[11 empty] | 10.06.2026 | 488 dt. 23.06.2026 | 730 | 1: 8.42; 2: 9.6; 3: 48; 5: 17; 11: 7; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 03.07.2026 | 583 dt. 10.07.2026 | 4434030.49 | 1: 5.91; 2: 6; 3: 40; 5: 9; 11: 1.27; 15: 0.56; 25: 90; 52: BDL(DL=02); 55: 729 |  |  | 0.8 | Complying | Complying | - | 7.5 | 110 | 380 |  | 155 | [9 empty] | 1.87 | [9 empty] | 1.14X105 | [26 empty] | 32.5 |  |  | 1442 |  |  | 6.3
2 | (YMN-STP-002) 20 MLD STP,Radaur Road, Yamuna Nagar by PHED March dt. 30.09.2019 |  | 10 | 5.5 to 9 | 50 | 10
[11 empty] | 09.01.2026 | 4284 dt. 21.01.2026 |  | 1: 7.04; 2: 5.2; 3: 36; 5: 9; 11: ND |  |  |  | Complying | Complying
[11 empty] | 17.02.2026 | 4543 dt. 02.03.2026 | 703 | 1: 7.8; 2: 6.5; 3: 40; 5: 9; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 17.03.2026 | 4726 dt.01.04.2026 | 640 | 1: 8.16; 2: 5.4; 3: 36; 5: 9; 11: 1.96; 25: 60 |  |  |  | Complying | Complying
[11 empty] | 10.04.2026 | 97 dt. 28.04.2026 | 7.66 | 1: 7.99; 2: 4.6; 3: 28; 5: 6; 11: 1.92; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 19.05.2026 | 286 dt. 01.06.2026 |  | 1: 7.62; 2: 8.2; 3: 44; 5: 17; 11: 9.807; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 10.06.2026 | 487 dt. 23.06.2026 | 140.37 | 1: 7.87; 2: 9.2; 3: 44; 5: 13; 11: 7.85; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 03.07.2026 | 582 dt. 10.07.2026 | 708 | 1: 7.3; 2: 7.5; 3: 36; 5: 12; 11: 1.28; 15: 1.85; 25: 60; 52: BDL(DL=02); 55: 719 |  |  |  | Complying | Complying |  | 7.54 | 112 | 372 |  | 208 | [5 empty] | 13.92 |  |  |  | 10.62 | [9 empty] | 1.13 X105 | [26 empty] | 32.5 |  |  | 1442
3 | (YMN-STP-003) 3 MLD STP Chhachhrauli, Yamuna Nagar by PHED in 31.12.2015 (MBBR+TT, 2019) |  | 10 | 7 to 8 | 50 | 20 | [68 empty] | 7.4 | 88 | 340 |  | 142 | [5 empty] | 11.47 |  |  | 0.22
[11 empty] | 27.01.2026 | 4367 dt. 09.02.2026 |  | 1: 7.16; 2: 7.8; 3: 44; 5: 15; 11: ND |  |  |  | Complying | Complying
[11 empty] | 25.02.2026 | 4588 dt. 10.03.2026 |  | 1: 8.05; 2: 6.5; 3: 32; 5: 10; 11: ND; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 06.03.2026 | 4647 dt.19.03.2026 |  | 1: 7.65; 2: 4.8; 3: 32; 5: 10; 11: BDL; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 10.04.2026 | 95 dt. 28.04.2026 |  | 1: 7.67; 2: 7.2; 3: 40; 5: 14; 11: 2.22; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 16.05.2026 | 268 dt. 27.05.2026 |  | 1: 7.9; 2: 14.2; 3: 68; 5: 11; 11: 20.4; 25: 900 |  |  |  | Non-Complying | Non-Complying
[11 empty] | 12.06.2026 | 496 dt. 24.06.2026 |  | 1: 8.45; 2: 17; 3: 84; 5: 29; 11: 43.43; 25: 90 |  |  |  | Non-Complying | Non-Complying |  | 8.37 | 54 | 172 |  | 49 | [5 empty] | 60.24 | [13 empty] | 1.24 X10
[11 empty] | 03.07.2026 | 586 dt. 10.07.2026 | 4434030.49 | 1: 7.19; 2: 7; 3: 40; 5: 12; 11: 3.29; 15: 0.19; 25: 70; 52: BDL(DL=02); 55: 1003 |  |  |  | Complying | Complying | - | 6.92 | 120 | 388 |  | 182 | [5 empty] | 14.21 |  |  |  | 7.41 | [9 empty] | 1.12 X105 | [26 empty] | 32.5 |  |  | 1442
4 | (YMN-STP-004) 24 MLD STP Parwalo, Yamuna Nagar by PHED in 31.12.2018 (SBR) |  | 10 | 5.5 to 9 | 100 | 10
[11 empty] | 07.01.2026 | 4225 dt. 15.01.2026 | 9115727 | 1: 6.99; 2: 5.4; 3: 28; 5: 7; 11: ND |  |  |  | Complying | Complying
[11 empty] | 03.02.2026 | 4411 dt. 10.02.2026 | 9377871 | 1: 7.4; 2: 8.6; 3: 48; 5: 18; 11: 2.46; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 06.03.2026 | 4645 dt.19.03.2026 | 9755873 | 1: 7.88; 2: 6.4; 3: 40; 5: 6; 11: BDL; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 10.04.2026 | 96 dt. 28.04.2026 | 282656 | 1: 7.73; 2: 6; 3: 32; 5: 11; 11: 1.92; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 22.05.2026 | 323 dt. 03.06.2026 | 989956.8 | 1: 7.59; 2: 13.6; 3: 68; 5: 27; 11: 36.426; 25: 200; 52: 8.5 |  |  |  | Non-complying | Non-complying
[11 empty] | 09.06.2026 | 469 dt. 22.06.2026 | 1298574 | 1: 7.8; 2: 6.5; 3: 32; 5: 9; 11: 2.47; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 03.07.2026 | 580 dt. 10.07.2026 | 1700514 | 1: 7.53; 2: 4.8; 3: 28; 5: 6; 11: ND; 15: ND; 25: 50; 52: BDL(DL=02); 55: 987 |  |  |  | Complying | Complying | - | 7.09 | 102 | 328 |  | 125 | [5 empty] | 12.48 |  |  |  | 3.9 | [9 empty] | 1.12X105 | [26 empty] | 32.5 |  |  | 1442
5 | (YMN-STP-005) 3.5 MLD STP Radaur, Yamuna Nagar by PHED 31.12.2015 (MBBR+TT, 2019) |  | 10 | 7 to 8 | 50 | 20
[11 empty] | 09.01.2026 | 4287 dt. 21.01.2026 |  | 1: 6.96; 2: 6.4; 3: 44; 5: 15; 11: ND |  |  |  | Complying | Complying
[11 empty] | 25.02.2026 | 4555 dt. 03.03.2026 | 49.2 | 1: 7.56; 2: 7.8; 3: 48; 5: 16; 11: ND; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 13.03.2026 | 4714 dt. 25.03.2026 |  | 1: 7.73; 2: 7.8; 3: 36; 5: 11; 11: ND; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 22.04.2026 | 157 dt. 29.04.2026 |  | 1: 7.76; 2: 6.7; 3: 28; 5: 8; 11: ND; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 27.05.2026 | 360 dt. 10.06.2026 |  | 1: 8.35; 2: 8.6; 3: 48; 5: 25; 11: 13.732; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 12.06.2026 | 495 dt. 24.06.2026 |  | 1: 7.91; 2: 8.2; 3: 44; 5: 11; 11: 15.41; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 01.07.2026 | 551 dt. 08.07.2026 |  | 1: 7.93; 2: 8.4; 3: 44; 5: 13; 11: 2.8; 15: 0.77; 25: 80; 52: BDL(DL=02); 55: 498 |  |  |  | Complying | Complying |  | 7.01 | 80 | 260 |  | 175 | [9 empty] | 4.49 | [9 empty] | 1.36X105 | [26 empty] | 32.5 |  |  | 1442
6 | (YMN-STP-006) 10 MLD STP Baddimajra , Yamuna Nagar, Unit-I by PHED 30.07.2019 (SBR) |  | 10 | 6.5-9.0 | 50 | 20
[11 empty] | 09.01.2026 | 4285 dt. 21.01.2026 |  | 1: 7; 2: 120; 3: 388; 5: 204; 11: 15.58 |  |  |  | Non-Complying | Non-Complying
[11 empty] | 17.02.2026 | 4539 dt. 02.03.2026 | 510 | 1: 7.85; 2: 5; 3: 28; 5: 9; 11: ND; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 17.03.2026 | 4728 dt.01.04.2026 | 7640 | 1: 7.79; 2: 4.4; 3: 28; 5: 9.5; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 09.04.2026 | 100 dt. 28.04.2026 | 8287 | 1: 7.74; 2: 7.6; 3: 48; 5: 15; 11: ND; 25: 60 |  |  |  | Complying | Complying
May, 2026
[11 empty] | 10.06.2026 | 487-A dt. 23.06.2026 |  | 1: 8.2; 2: 6; 3: 32; 5: 5; 11: 17.85; 25: 90 |  |  |  | Complying | Complying
7 | (YMN-STP-007) 10 MLD STP at Baddimajra, Unit-II, Yamuna Nagar by PHED dt. 31.07.2021
[11 empty] | 09.01.2026 | 4286 dt. 21.01.2026 |  | 1: 7.03; 2: 6.2; 3: 32; 5: 13; 11: ND |  |  |  | Complying | Complying
[11 empty] | 17.02.2026 | 4540 dt. 02.03.2026 | 855 | 1: 7.62; 2: 5.8; 3: 32; 5: 8; 11: ND; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 17.03.2026 | 4729 dt.01.04.2026 | 7463 | 1: 7.39; 2: 8; 3: 48; 5: 15; 11: 4.76; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 10.04.2026 | 98 dt. 28.04.2026 | 640.93 | 1: 7.65; 2: 5; 3: 32; 5: 7; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 19.05.2026 | 288 dt. 01.06.2026 |  | 1: 7.54; 2: 28; 3: 96; 5: 33; 11: 28.02; 25: 3.8 X103 |  |  |  | Non-complying | Non-complying
[11 empty] | 19.05.2026 | 288 dt. 01.06.2026 (bypass through portable pipe) |  | 1: 7.29; 2: 410; 3: 1224; 5: 398; 11: 585.618; 25: 4.6 X105 |  |  |  | Non-complying | Non-complying
[11 empty] | 10.06.2026 | 489 dt. 23.06.2026 |  | 1: 7.96; 2: 8.2; 3: 44; 5: BDL; 11: 6.04; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 03.07.2026 | 581 dt. 10.07.2026 |  | 1: 6.89; 2: 13; 3: 64; 5: 29; 11: 12.78; 15: 3.83; 25: 400; 52: 3.5; 55: 878 |  |  |  | Non-complying | Non-complying |  | 6.69 | 180 | 620 |  | 428 | [5 empty] | 18.96 |  |  |  | 18.33 | [9 empty] | 1.85X105 | [26 empty] | 32.5 |  |  | 1442
8 | 01 MLD STP, PHED, Patashgarh, Yamunanagar
[11 empty] | 28.01.2026 | 4368 dt. 09.02.2026 |  | 1: 7.28; 2: 7.2; 3: 48; 5: 13; 11: ND |  |  |  | Complying | Complying
[11 empty] | 17.02.2026 | 4541 dt. 02.03.2026 |  | 1: 7.57; 2: 7.2; 3: 40; 5: 11; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 17.03.2026 | 4725 dt. 01.04.2026 |  | 1: 7.76; 2: 7.8; 3: 44; 5: 12; 11: 2.96; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 09.04.2026 | 101 dt. 28.04.2026 |  | 1: 7.89; 2: 7; 3: 40; 5: 16; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 19.05.2026 | 289 dt. 01.06.2026 |  | 1: 7.62; 2: 9.2; 3: 48; 5: 16; 11: 6.732; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 10.06.2026 | 486 dt. 23.06.2026 |  | 1: 7.92; 2: 5.8; 3: 32; 5: 9; 11: 13.47; 25: 40 |  |  |  | Complying | Complying
[11 empty] | 14.07.2026 | 656 dt. 21.07.2026 |  | 1: 7.4; 2: 7.8; 3: 40; 5: 12; 11: 3.78; 15: BDL(DL=0.4); 25: 80; 52: BDL(DL=02); 55: 730 |  |  |  | Complying | Complying |  | 7.28 | 110 | 424 |  | 198 | [9 empty] | 2.42 | [9 empty] | 1.2X105 | [26 empty] | 32.5 |  |  | 1442
Karnal
9 | (KRN-STP-11) 50 MLD STP, Transport Nagar, Karnal by ULBD in 31.08.2020 (SBR)
[11 empty] | 06.01.2026 | 4197 dt. 15.01.2026 | 2791 | 1: 7.32; 2: 6.2; 3: 32; 5: 11; 11: ND |  |  |  | Complying | Complying |  | 6.92 | 120 | 408 |  | 232 | [5 empty] | 14.23
[11 empty] | 04.02.2026 | 4421 dt. 16.02.2026 |  | 1: 7.26; 2: 7.2; 3: 36; 5: 14; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 6.94 | 130 | 424 |  | 208 | [5 empty] | 14.82 | [13 empty] | -
[11 empty] | 09.03.2026 | 4680 dt. 24.03.2026 |  | 1: 7.56; 2: 4.4; 3: 24; 5: 7; 11: ND; 25: BDL(DL=02) |  |  |  | Complying | Complying |  | 7.1 | 98 | 308 |  | 132 | [5 empty] | 11.84 | [13 empty] | -
[11 empty] | 09.04.2026 | 86 dt. 24.04.2026 | 2930 | 1: 7.25; 2: 7.8; 3: 48; 5: 13; 11: ND; 25: 90 |  |  |  | Complying | Complying | 17744 | 6.86 | 120 | 420 |  | 230 | [5 empty] | 13.28 | [13 empty] | -
[11 empty] | 18.05.2026 | 279 dt. 29.05.2026 | 2688.5 | 1: 8.11; 2: 8; 3: 40; 5: 15; 11: 1.38; 25: 80 |  |  |  | Complying | Complying | 2130 | 7.7 | 130 | 428 |  | 188 | [5 empty] | 19.38 | [13 empty] | -
[11 empty] | 05.06.2026 | 442 dt. 16.06.2026 | 2781.99 | 1: 7.96; 2: 5; 3: 28; 5: 11; 11: -; 25: 80 |  |  |  | Complying | Complying | 2326.5 | 7.59 | 135 | 460 |  | 208 | [5 empty] | - | [13 empty] | -
| July, 2026 1st Phase | [9 empty] | 04.07.2026 | 596 dt.13.07.2026 | 275 | 1: 7.58; 2: 7; 3: 28; 5: 8; 25: 80; 52: BDL |  |  |  | Complying | Complying | 1936.7 | 7.1 | 108 | 352 |  | 158 | [19 empty] | 1.22X105 | [26 empty] | 21.5
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | 730 dt. 05.08.2026 |  | 1: 7.8; 2: 6.8; 3: 32; 5: 9; 6: 358; 7: 70.47; 9: 96.44; 12: ND; 13: ND; 14: ND; 16: ND; 17: ND; 18: 78.2; 19: 100; 20: 172; 23: 208; 24: 272; 25: 80; 28: 1.57; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: 1.223; 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: BDL(DL=02); 55: 652 |  |  |  | Complying | Complying |  | 7.6 | 96 | 308 |  | 152 | 990 | 103.96 |  | 328.36 |  |  | 17.32 | 12.83 | 4.87 |  | 152 | ND | 186.8 | 308 | 188 |  |  | 402 | 496 | 1.23X105 |  |  | 2.68 |  |  | BDL(DL=0.001) | BDL(DL=0.230) | 9.872 | BDL(DL=0.07) | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | BDL(DL=0.5243) | BDL(DL=0.001) | [8 empty] | 25 |  |  | 652
August, 1st Phase, 2026
August, 2nd Phase, 2026
10 | (KRN-STP-003) 8 MLD STP RK Puram Karnal by ULBD in March dt. 31.10.2019 (SBR)
[11 empty] | 09.01.2026 | 4275 dt. 21.01.2026 |  | 1: 7.26; 2: 18; 3: 92; 5: 23; 11: 4.89 |  |  |  | Non- Complying | Non- Complying |  | 6.87 | 110 | 388 |  | 138 | [5 empty] | 13.44
[11 empty] | 10.02.2026 | 4472 dt. 23.02.2026 |  | 1: 8.06; 2: 7.5; 3: 44; 5: 11 |  |  |  | Complying | Complying |  | 7.02 | 108 | 380 |  | 168
[11 empty] | 09.03.2026 | 4678 dt. 24.03.2026 |  | 1: 7.48; 2: 5.8; 3: 32; 5: 8; 11: BDL; 25: 50 |  |  |  | Complying | Complying |  | 7.2 | 102 | 348 |  | 108 | [5 empty] | 16.28 | [13 empty] | -
[11 empty] | 09.04.2026 | 47 dt. 22.04.2026 |  | 1: 7.12; 2: 6; 3: 32; 5: 7; 11: ND; 25: 60 |  |  |  | Complying | Complying |  | 6.89 | 120 | 396 |  | 188 | [5 empty] | 14.97 | [13 empty] | -
[11 empty] | 18.05.2026 | 235 dt. 20.05.2026 |  | 1: 8.1; 2: 13; 3: 56; 5: 30; 11: 3.78; 25: 90 |  |  |  | Non- Complying | Non- Complying |  | 8.17 | 12 | 340 |  | 156 | [5 empty] | 13.08 | [13 empty] | -
[11 empty] | 05.06.2026 | 445 dt. 16.06.2026 |  | 1: 7.6; 2: 8.2; 3: 48; 5: 15; 25: 90 |  |  |  | Complying | Complying |  | 7.46 | 125 | 412 |  | 195 | [19 empty] | -
| July, 2026 1st Phase | [9 empty] | 04.07.2026 | 599 dt.13.07.2026 | 40.24 | 1: 7.16; 2: 6.2; 3: 32; 5: 11; 25: 90; 52: BDL |  |  |  | Complying | Complying | 160.42 | 7.12 | 110 | 364 |  | 186 | [19 empty] | 1.22X105 | [26 empty] | 19.5
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | 732 dt. 05.08.2026 |  | 1: 7.94; 2: 6.4; 3: 32; 5: 12; 6: 330; 7: 23.99; 9: 147.18; 12: ND; 13: ND; 14: ND; 16: ND; 17: ND; 18: 42.8; 19: 92; 20: 164; 23: 142; 24: 256; 25: 90; 28: 1.48; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: 0.725; 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: BDL(DL=02); 55: 1008 |  |  |  | Complying | Complying |  | 7.59 | 120 | 412 |  | 175 | 1020 | 61.98 |  | 312.68 |  |  | 21.94 | 14.98 | 2.84 |  | 4.6 | ND | 73.8 | 124 | 200 |  |  | 328 | 324 | 1.19X105 |  |  | 4.13 |  |  | BDL(DL=0.001) | BDL(DL=0.230) | 6.382 | BDL(DL=0.07) | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | BDL(DL=0.5243) | BDL(DL=0.001) | [8 empty] | 22 |  |  | 1870
11 | (KRN-STP-004) 7 MLD STP Gharaunda , Karnal by PHED in March 31.05.2019 (SBR) | Deptt. | 10 | 7-8.0 | 50 | 20
[11 empty] | 09.01.2026 | 4272 dt. 21.01.2026 |  | 1: 7.69; 2: 5.6; 3: 40; 5: 11; 11: ND |  |  |  | Complying | Complying |  | 6.97 | 130 | 472 |  | 292 | [5 empty] | 11.78
[11 empty] | 17.02.2026 | 4530 dt. 02.03.2026 |  | 1: 7.16; 2: 13; 3: 60; 5: 25; 11: ND |  |  |  | Non- Complying | Non- Complying |  | 7.68 | 120 | 396 |  | 164 | [5 empty] | 14.96 | [13 empty] | -
[11 empty] | 17.03.2026 | 4755 dt. 02.04.2026 |  | 1: 7.69; 2: 6.8; 3: 36; 5: 11; 11: ND; 25: 70 |  |  |  | Complying | Complying |  | 7.34 | 125 | 408 |  | 225 | [5 empty] | 13.82 | [13 empty] | -
[11 empty] | 08.04.2026 | 91 dt. 24.04.2026 |  | 1: 7.3; 2: 6.6; 3: 40; 5: 13; 11: ND; 25: 60 |  |  |  | Complying | Complying |  | - | - | - |  | - | [5 empty] | 10 | [13 empty] | -
[11 empty] | 27.05.2026 | 363 dt. 10.06.2026 |  | 1: 8.08; 2: 6.5; 3: 28; 5: 8; 11: 7.08; 25: 80 |  |  |  | Complying | Complying |  | 8.7 | 98 | 320 |  | 156 | [5 empty] | 18.97 | [13 empty] | -
[11 empty] | 03.06.2026 | 411 dt. 15.06.2026 |  | 1: 7.86; 2: 5.2; 3: 28; 5: 9.5; 11: 7.88; 25: ND |  |  |  | Complying | Complying |  | - | - | - |  | - | [5 empty] | - | [13 empty] | -
| July, 2026 1st Phase | [9 empty] | 02.07.2026 | 566 dt. 09.07.2026 | 254 | 1: 7.64; 2: 8.2; 3: 44; 5: 13; 25: 90 |  |  |  | Complying | Complying | 413 | 7.82 | 72 | 224 |  | 143 | [19 empty] | 1.25X105 | [26 empty] | 19.5
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | 734 dt. 05.08.2026 |  | 1: 7.56; 2: 5.6; 3: 20; 5: 9; 6: 610; 7: 71.97; 9: 166.51; 12: ND; 13: ND; 14: ND; 16: ND; 17: ND; 18: 68.6; 19: 105.4; 20: 170.6; 23: 102; 24: 276; 25: 60; 28: 1.23; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: BDL(DL=0.264); 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: BDL(DL=02); 55: 1120 |  |  |  | Complying | Complying |  | 7.65 | 92 | 308 |  | 156 | 682 | 109.96 |  | 333.37 |  |  | 12.54 | 9.38 | 4.68 |  | 6.4 | ND | 72.4 | 157.8 | 198.2 |  |  | 344 | 356 | 1.27 X105 |  |  | 2.95 |  |  | BDL(DL=0.001) | BDL(DL=0.230) | BDL(DL=0.264) | BDL(DL=0.07) | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | BDL(DL=0.5243) | BDL(DL=0.001) | [8 empty] | 22 |  |  | 1243
12 | (KRN-STP-005) 10 MLD STP at Gogari Road, Karnal by ULBD on 01.03.2018 (SBR)
[11 empty] | 09.01.2026 | 4279 dt. 21.01.2026 |  | 1: 7.06; 2: 4.8; 3: 28; 5: 9; 11: ND |  |  |  | Complying | Complying |  | 7.04 | 120 | 424 |  | 164 | [5 empty] | 12.78
[11 empty] | 10.02.2026 | 4470 dt. 23.02.2026 |  | 1: 7.74; 2: 6.5; 3: 32; 5: 11; 11: 12.78; 25: 90 |  |  |  | Complying | Complying |  | 7.06 | 105 | 372 |  | 158 | [5 empty] | 12.78 | [13 empty] | -
[11 empty] | 25.03.2026 | 4708 dt. 25.03.2026 | 205 | 1: 8.03; 2: 6.2; 3: 36; 5: 11; 11: 4.89; 25: 90 |  |  |  | Complying | Complying | 375 | 6.82 | 112 | 376 |  | 172 | [5 empty] | 16.52 | [13 empty] | -
[11 empty] | 06.04.2026 | 46 dt. 22.04.2026 | 50 | 1: 7.1; 2: 5.5; 3: 28; 5: 8; 11: ND; 25: 80 |  |  |  | Complying | Complying | 592 | 7.01 | 102 | 356 |  | 205 | [5 empty] | 13.86 | [13 empty] | -
[11 empty] | 11.05.2026 | 238 dt. 20.05.2026 |  | 1: 8.27; 2: 12; 3: 64; 5: 18; 11: ND; 25: 80 |  |  |  | Non-Complying | Non-Complying |  | 7.96 | 98 | 330 |  | 152 | [5 empty] | 13.86 | [13 empty] | -
[11 empty] | 05.06.2026 | 444 dt. 16.06.2026 |  | 1: 7.71; 2: 7.2; 3: 40; 5: 13; 25: 70 |  |  |  | Complying | Complying |  | 7.49 | 120 | 408 |  | 156 | [5 empty] | 14.56 | [13 empty] | -
| July, 2026 1st Phase | [9 empty] | 04.07.2026 | 598 dt.13.07.2026 | 75.47 | 1: 7.59; 2: 6.8; 3: 44; 5: 13; 25: 70; 52: BDL |  |  |  | Complying | Complying | 308.33 | 6.86 | 106 | 368 |  | 176 | [19 empty] | 1.26X105 | [26 empty] | 23
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | 726 dt. 05.08.2026 |  | 1: 8.01; 2: 6.5; 3: 44; 5: 9; 6: 324; 7: 81.97; 9: 160.67; 12: ND; 13: ND; 14: ND; 16: ND; 17: ND; 18: 60.8; 19: 90; 20: 178; 23: 122; 24: 268; 25: 50; 28: 2.02; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: 0.8324; 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: BDL(DL=02); 55: 590 |  |  |  | Complying | Complying |  | 6.98 | 108 | 364 |  | 185 | 880 | 106.96 |  | 242.93 |  |  | 19.48 | 23.15 | 3.87 |  | 6.4 | ND | 178.2 | 200 | 192 |  |  | 280 | 452 | 1.25X105 |  |  | 4.48 |  |  | BDL(DL=0.001) | BDL(DL=0.230) | 2.832 | 1.723 | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | BDL(DL=0.5243) | BDL(DL=0.001) | [8 empty] | 23 |  |  | 1610
13 | (KRN-STP-012) 4 MLD STP Indri, Karnal by PHED in April, 2021 (SBR) | RO | <10 | 5.5-9.0 | 100 | <20 | <10 |  |  | <100
[11 empty] | 17.02.2026 | 4528 dt. 02.03.2026 | 196.88 | 1: 7.92; 2: 6.2; 3: 32; 5: 7; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 7.26 | 125 | 420 |  | 178 | [5 empty] | 13.62 | [13 empty] | -
[11 empty] | 10.03.2026 | 4693 dt. 24.03.2026 |  | 1: 7.63; 2: 7.8; 3: 48; 5: 16; 11: ND |  |  |  | Complying | Complying
[11 empty] | 17.04.2026 | 152 dt. 29.04.2026 |  | 1: 8.27; 2: 5.58; 3: 36; 5: 14; 11: ND; 25: 50 |  |  |  | Complying | Complying |  | 7.8 | 102 | 340 |  | 116 | [5 empty] | 12.56 | [13 empty] | -
[11 empty] | 27.05.2026 | 364 dt. 10.06.2026 |  | 1: 8.91; 2: 5.8; 3: 28; 5: 8; 11: 4.75; 25: 70 |  |  |  | Complying | Complying |  | 8.33 | 95 | 312 |  | 145 | [5 empty] | 21.26 | [13 empty] | -
[11 empty] | 03.06.2026 | 412 dt. 15.06.2026 |  | 1: 7.86; 2: 5.6; 3: 32; 5: 12; 11: 9.08 |  |  |  | Complying | Complying
| July, 2026 1st Phase | [9 empty] | 04.07.2026 | 595 dt.13.07.2026 | 120.77 | 1: 7.23; 2: 5.8; 3: 32; 5: 9; 25: 50; 52: BDL |  |  |  | Complying | Complying | 130.5 | 7.05 | 104 | 340 |  | 224 | [19 empty] | 1.21X105 | [26 empty] | 24
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | 735 dt. 05.08.2026 |  | 1: 6.98; 2: 7.5; 3: 40; 5: 8; 6: 492; 7: 79.97; 9: 75.41; 12: ND; 13: 1.72; 14: ND; 16: ND; 17: ND; 18: 56.4; 19: 93.6; 20: 62.4; 23: 102; 24: 156; 25: 70; 28: 1.95; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: BDL(DL=0.264); 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: BDL(DL=02); 55: 906 |  |  |  | Complying | Complying |  | 7.47 | 125 | 400 |  | 135 | 552 | 91.97 |  | 209.23 |  |  | 20.42 | 12.08 | 1.93 |  | 3.6 | ND | 88.2 | 131.8 | 88.7 |  |  | 296 | 220 | 1.17X105 |  |  | 2.57 |  |  | BDL(DL=0.001) | BDL(DL=0.230) | BDL(DL=0.264) | BDL(DL=0.07) | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | BDL(DL=0.5243) | BDL(DL=0.001) | [8 empty] | 22.5 |  |  | 1016
14 | (KRN-STP-007) 6 MLD STP Nilokheri, Karnal by PHED in 1.8.2014 (MBBR+TT, 2019) | Deptt. | 10 | 7-8.00 | 50 | 20
[11 empty] | 06.01.2026 | 4198 dt. 15.01.2026 | 241.2 | 1: 8.01; 2: 14; 3: 68; 5: 24; 11: 7.22 |  |  |  | Non-Complying | Non-Complying |  | 7.84 | 110 | 392 |  | 195 | [5 empty] | 15.32
[11 empty] | 10.02.2026 | 4468 dt. 23.02.2026 | 248 | 1: 7.83; 2: 15; 3: 76; 5: 29; 11: 8.79 |  |  |  | Non-Complying | Non-Complying |  | 7.06 | 125 | 452 |  | 168 | [5 empty] | 13.52 | [13 empty] | -
[11 empty] | 10.03.2026 | 4691 dt. 24.03.2026 | 497 | 1: 7.9; 2: 23; 3: 104; 5: 52; 11: 8.64; 25: 900 |  |  |  | Non-Complying | Non-Complying |  | 6.92 | 145 | 488 |  | 320 | [5 empty] | 17.93 | [13 empty] | -
[11 empty] | 06.04.2026 | 49 dt. 22.04.2026 |  | 1: 7.08; 2: 22; 3: 108; 5: 72; 11: 9.68; 25: 1100 |  |  |  | Non-Complying | Non-Complying |  | 6.97 | 125 | 452 |  | 215 | [5 empty] | 15.98 | [13 empty] | -
[11 empty] | 18.05.2026 | 280 dt. 29.05.2026 | 256 | 1: 8.04; 2: 7.2; 3: 36; 5: 13; 11: 1.86; 25: 80 |  |  |  | Complying | Complying | 326 | 7.69 | 120 | 388 |  | 192 | [5 empty] | 14.38 | [13 empty] | -
[11 empty] | 05.06.2026 | 447 dt. 15.06.2026 | 245 | 1: 7.7; 2: 6.8; 3: 32; 5: 10; 25: 50 |  |  |  | Complying | Complying | 267 | 7.7 | 120 | 400 |  | 118 | [19 empty] | -
| July, 2026 1st Phase | [9 empty] | 02.07.2026 | 565 dt. 09.07.2026 | 260 | 1: 7.08; 2: 5.3; 3: 28; 5: 7; 11: 8.4; 25: 50; 52: BDL |  |  |  | Complying | Complying | 285 | 7.28 | 119 | 372 |  | 218 | [5 empty] | 21.01 | [13 empty] | 1.28X105 | [26 empty] | 27.5
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | 736 dt. 05.08.2026 |  | 1: 7.67; 2: 5.8; 3: 36; 5: 10; 6: 352; 7: 37.98; 9: 185.53; 12: ND; 13: 2.83; 14: ND; 16: ND; 17: ND; 18: 58; 19: 86; 20: 150; 23: 340; 24: 236; 25: 70; 28: 1.95; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: 1.088; 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: BDL(DL=02); 55: 642 |  |  |  | Complying | Complying |  | 7.57 | 110 | 372 |  | 158 | 1020 | 69.97 |  | 352.39 |  |  | 13.94 | 9.86 | 3.28 |  | 16 | ND | 58 | 86 | 150 |  |  | 128 | 236 | 1.18X105 |  |  | 2.14 |  |  | BDL(DL=0.001) | BDL(DL=0.230) | 4.182 | BDL(DL=0.07) | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | BDL(DL=0.5243) | BDL(DL=0.001) | [8 empty] | 23 |  |  | 642
15 | (KRN-STP-008) 4 MLD, Nissing Karnal by PHED in 10.8.2016 (MBBR+TT, 2020) | Deptt. | 10 | 7-8.00 | 50 | 20
[11 empty] | 09.01.2026 | 4273 dt. 21.01.2026 |  | 1: 7.76; 2: 3.8; 3: 24; 5: 7; 11: ND |  |  |  | Complying | Complying |  | 6.97 | 105 | 380 |  | 255 | [5 empty] | 14.52
[11 empty] | 02.03.2026 | 4529 dt. 02.03.2026 | 83.3 | 1: 7.57; 2: 9; 3: 48; 5: 18; 11: ND; 25: 90 |  |  |  | Complying | Complying | 13.8 | 7.7 | 102 | 352 |  | 145 | [5 empty] | 12.68 | [13 empty] | -
[11 empty] | 12.03.2026 | 4707 dt. 25.03.2026 | 104 | 1: 8.05; 2: 8.8; 3: 48; 5: 18; 11: 6.72; 25: 90 |  |  |  | Complying | Complying | 137 | 7.8 | 110 | 380 |  | 182 | [5 empty] | 17.84 | [13 empty] | -
[11 empty] | 08.04.2026 | 92 dt. 24.04.2026 |  | 1: 7.18; 2: 7.2; 3: 48; 5: 15; 11: ND; 25: 70 |  |  |  | Complying | Complying |  | 6.63 | 120 | 392 |  | 192 | [5 empty] | 13.42 | [13 empty] | -
[11 empty] | 11.05.2026 | 237 dt. 20.05.2026 |  | 1: 8.15; 2: 13; 3: 60; 5: 26; 11: 1.96; 25: 70 |  |  |  | Non-Complying | Non-Complying |  | 8.2 | 102 | 356 |  | 175 | [19 empty] | -
[11 empty] | 05.06.2026 | 437 dt. 16.06.2026 |  | 1: 8.13; 2: 6.8; 3: 44; 5: 12; 25: 80 |  |  |  | Complying | Complying |  | 7.84 | 120 | 396 |  | 155
| July, 2026 1st Phase | [9 empty] | 04.07.2026 | 602 dt. 13.07.2026 | 1120 | 1: 7.07; 2: 6.8; 3: 44; 5: 15; 25: 70; 52: BDL |  |  |  | Complying | Complying | 1249 | 7.14 | 112 | 384 |  | 185 | [19 empty] | 1.25X105 | [26 empty] | 26.5
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | 724 dt. 05.08.2026 |  | 1: 7.4; 2: 15; 3: 72; 5: 23; 6: 750; 7: 49.98; 9: 190.54; 12: 5.08; 13: 9.64; 14: ND; 16: ND; 17: ND; 18: 63.6; 19: 170; 20: 164; 23: 224; 24: 284; 25: 900; 28: 1.62; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: 1.082; 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: 3; 55: 1369 |  |  |  | Non-Complying | Non-Complying |  | 7.76 | 135 | 452 |  | 190 | 780 | 137.97 |  | 357.89 |  |  | 19.72 | 18.23 | 2.89 |  | 8 | ND | 180.3 | 172 | 190 |  |  | 388 | 362 | 1.38X105 |  |  | 3.44 |  |  | BDL(DL=0.001) | BDL(DL=0.230) | 6.892 | 0.803 | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | BDL(DL=0.5243) | BDL(DL=0.001) | [8 empty] | 22.5 |  |  | 1420
16 | (KRN-STP-009) 5.5 MLD STP Taraori, Karnal by PHED in 1.6.2016 (MBBR+TT, 2019) | Deptt. | 10 | 7-8.0 | 50 | 20
[11 empty] | 10.02.2026 | 4469 dt. 23.02.2026 | 242 | 1: 7.75; 2: 13; 3: 68; 5: 25; 11: 9.72; 25: 500 |  |  |  | Non-Complying | Non-Complying | 302 | 7.13 | 130 | 460 |  | 263 | [5 empty] | 16.75 | [13 empty] | -
[11 empty] | 10.03.2026 | 4692 dt. 24.03.2026 |  | 1: 7.75; 2: 36; 3: 168; 5: 30; 11: ND; 25: 600 |  |  |  | Non-Complying | Non-Complying |  | 7.12 | 160 | 512 |  | 308 | [5 empty] | 15.93 | [13 empty] | -
[11 empty] | 06.04.2026 | 48 dt. 22.04.2026 |  | 1: 7.1; 2: 25; 3: 124; 5: 89; 11: 10.48; 25: 800 |  |  |  | Non-Complying | Non-Complying |  | 6.89 | 105 | 376 |  | 178 | [5 empty] | 13.48 | [13 empty] | -
[11 empty] | 18.05.2026 | 281 dt. 29.05.2026 |  | 1: 8.04; 2: 15; 3: 80; 5: 28; 11: 12.08; 25: 400 |  |  |  | Non-Complying | Non-Complying |  | 7.7 | 125 | 412 |  | 168 | [5 empty] | 10.48 | [13 empty] | -
[11 empty] | 05.06.2026 | 846 dt. 16.06.2026 |  | 1: 7.74; 2: 13; 3: 68; 5: 25; 11: -; 25: 200 |  |  |  | Non-Complying | Non-Complying |  | 7.59 | 140 | 480 |  | 205 | [5 empty] | 12.08 | [13 empty] | -
| July, 2026 1st Phase | [9 empty] | 02.07.2026 | 564 dt. 09.07.2026 | 195 | 1: 7.23; 2: 14; 3: 76; 5: 26; 11: 18.21; 25: 400; 52: 3 |  |  |  | Non-Complying | Non-Complying |  | 7.3 | 108 | 340 |  | 200 | [5 empty] | 68.32 | [13 empty] | 1.28X105 | [26 empty] | 28.5
| July, 2026 2nd Phase | [9 empty] | 22.07.2026 | 723 dt. 05.08.2026 |  | 1: 7.37; 2: 13; 3: 68; 5: 27; 6: 520; 7: 27.99; 9: 203.72; 12: 4.28; 13: 11.28; 14: 0.98; 16: 1.6; 17: ND; 18: 80.8; 19: 102; 20: 180; 23: 204; 24: 282; 25: 400; 28: 2.43; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: 0.8623; 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: 2.5; 55: 953 |  |  |  | Non-Complying | Non-Complying |  | 7.56 | 92 | 304 |  | 182 | 562 | 59.98 |  | 243.27 |  |  | 24.53 | 24.97 | 6.81 |  | 11.2 | ND | 136.2 | 162 | 188 |  |  | 480 | 350 | 1.82X105 |  |  | 4.08 |  |  | BDL(DL=0.001) | BDL(DL=0.230) | 7.282 | 0.812 | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | BDL(DL=0.5243) | BDL(DL=0.001) | [8 empty] | 20.5 |  |  | 1024
17 | (KRN-STP-013) 20 MLD STP Phooshgarh, Karnal by ULBD in 06.06.2024 | [73 empty] | 6.14 | 102 | 352 |  | 168 | [5 empty] | 10.88
[11 empty] | 09.01.2026 | 4276 dt. 21.01.2026 |  | 1: 7.68; 2: 4; 3: 24; 5: 7; 11: ND |  |  |  | Complying | Complying |  | 6.89 | 120 | 408 |  | 218 | [5 empty] | 12.54
[11 empty] | 04.02.2026 | 4420 dt. 16.02.2026 |  | 1: 7.76; 2: 7; 3: 40; 5: 13; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 6.97 | 120 | 392 |  | 172 | [5 empty] | 14.52 | [13 empty] | -
[11 empty] | 09.03.2026 | 4676 dt. 24.03.2026 |  | 1: 7.37; 2: 8.4; 3: 44; 5: 6; 11: BDL(DL=02); 25: 90 |  |  |  | Complying | Complying |  | 7.37 | 130 | 372 |  | 6 | [5 empty] | 14.25 | [13 empty] | -
[11 empty] | 02.04.2026 | 24 dt. 17.04.2026 |  | 1: 8.12; 2: 6.2; 3: 40; 5: 11; 11: ND; 25: 60 |  |  |  | Complying | Complying |  | 8.12 | 145 | 496 |  | 11 | [5 empty] | 17.89 | [13 empty] | -
[11 empty] | 18.05.2026 | 276 dt. 29.05.2026 |  | 1: 7.9; 2: 6.4; 3: 32; 5: 10; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 7.9 | 110 | 384 |  | 10 | [5 empty] | 12.28 | [13 empty] | -
[11 empty] | 05.06.2026 | 439 dt. 16.06.2026 |  | 1: 7.7; 2: 5.8; 3: 40; 5: 9; 25: 80 |  |  |  | Complying | Complying |  | 7.7 | 102 | 380 |  | 9 | [19 empty] | -
| July, 2026 1st Phase | [9 empty] | 04.07.2026 | 604 dt. 13.07.2026 | 210.37 | 1: 7.17; 2: 7.4; 3: 44; 5: 12; 25: 80; 52: BDL |  |  |  | Complying | Complying | 872 | 6.88 | 120 | 388 |  | 180 | [19 empty] | 1.27X105 | [26 empty] | 23
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | 727 dt. 05.08.2026 |  | 1: 7.29; 2: 7.8; 3: 40; 5: 15; 6: 360; 7: 75.97; 9: 140.99; 12: ND; 13: ND; 14: ND; 16: ND; 17: ND; 18: 70.6; 19: 98; 20: 162; 23: 132; 24: 260; 25: 80; 28: 2.39; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: 0.896; 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: BDL(DL=02); 55: 659 |  |  |  | Complying | Complying |  | 7.39 | 130 | 432 |  | 205 | 432 | 107.96 |  | 291.32 |  |  | 9.72 | 18.72 | 3.61 |  | 4.8 | ND | 182.4 | 174 | 184 |  |  | 392 | 358 | 1.18X105 |  |  | 2.21 |  |  | BDL(DL=0.001) | BDL(DL=0.230) | 3.682 | BDL(DL=0.07) | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | BDL(DL=0.5243) | BDL(DL=0.001) | [8 empty] | 26.5 |  |  | 789
18 | (KRN-STP-014) 2 MLD STP Village Kachwa, Karnal
[11 empty] | 09.01.2026 | 4278 dt. 21.01.2026 |  | 1: 7.6; 2: 7.8; 3: 48; 5: 17; 11: ND |  |  |  | Complying | Complying |  | 6.99 | 140 | 480 |  | 288 | [5 empty] | 12.56
[11 empty] | 10.02.2026 | 4471 dt. 23.02.2026 | 169.9 | 1: 7.98; 2: 6; 3: 32; 5: 12; 11: ND; 25: 70 |  |  |  | Complying | Complying | 175.98 | 7.06 | 102 | 380 |  | 172 | [5 empty] | 14.29 | [13 empty] | -
[11 empty] | 09.03.2026 | 4679 dt. 24.03.2026 |  | 1: 7.5; 2: 6.4; 3: 40; 5: 9; 11: BDL(DL=02); 25: 70 |  |  |  | Complying | Complying |  | 7.23 | 140 | 416 |  | 154 | [5 empty] | 17.36 | [13 empty] | -
[11 empty] | 08.04.2026 | 88 dt. 22.04.2026 |  | 1: 7.28; 2: 5; 3: 28; 5: 8; 11: ND; 25: 50 |  |  |  | Complying | Complying |  | 7.13 | 110 | 360 |  | 228 | [5 empty] | 12.36 | [13 empty] | -
[11 empty] | 18.05.2026 | 275 dt. 29.05.2026 |  | 1: 8.17; 2: 5.6; 3: 28; 5: 9; 11: ND |  |  |  | Complying | Complying |  | 7.74 | 102 | 328 |  | 172 | [5 empty] | 12.03 | [13 empty] | -
[11 empty] | 05.06.2026 | 443 dt. 16.06.2026 |  | 1: 7.82; 2: 7; 3: 36; 5: 9; 25: 80 |  |  |  | Complying | Complying |  | 7.63 | 102 | 340 |  | 112 | [5 empty] | - | [13 empty] | -
| July, 2026 1st Phase | [9 empty] | 04.07.2026 | 600 dt.13.07.2026 | 32.54 | 1: 7.62; 2: 7.2; 3: 40; 5: 12; 25: 50; 52: BDL |  |  |  | Complying | Complying | 127.2 | 7.07 | 120 | 396 |  | 148 | [19 empty] | 1.77X105 | [26 empty] | 17.5
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | 729 dt. 05.08.2026 |  | 1: 8.16; 2: 5.2; 3: 28; 5: 8; 6: 558; 7: 58.98; 9: 164.68; 12: ND; 13: ND; 14: ND; 16: ND; 17: ND; 18: 70; 19: 90; 20: 178; 23: 104; 24: 268; 25: 80; 28: 2.33; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: 1.082; 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: BDL(DL=02); 55: 1016 |  |  |  | Complying | Complying |  | 7.59 | 120 | 412 |  | 175 | 1020 | 61.98 |  | 312.68 |  |  | 21.94 | 14.98 | 2.84 |  | 4.6 | ND | 73.8 | 124 | 200 |  |  | 328 | 324 | 1.19X105 |  |  | 4.13 |  |  | BDL(DL=0.001) | BDL(DL=0.230) | 6.382 | BDL(DL=0.07) | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | BDL(DL=0.5243) | BDL(DL=0.001) | [8 empty] | 22 |  |  | 1870
19 | (KRN-STP-015) 8 MLD STP Shiv Colony, Karnal by ULBD 31.10.2024
[11 empty] | 09.01.2026 | 4277 dt. 21.01.2026 |  | 1: 7.67; 2: 4.2; 3: 28; 5: 9; 11: ND |  |  |  | Complying | Complying |  | 6.9 | 115 | 408 |  | 240 | [5 empty] | 13.76
[11 empty] | 04.02.2026 | 4418 dt. 16.02.2026 |  | 1: 7.57; 2: 7.8; 3: 36; 5: 15; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 6.95 | 122 | 396 |  | 158 | [5 empty] | 17.39
[11 empty] | 09.03.2026 | 4677 dt. 24.03.2026 |  | 1: 7.49; 2: 5.8; 3: 32; 5: 8; 11: ND; 25: 50 |  |  |  | Complying | Complying |  | 7.19 | 120 | 404 |  | 148 | [5 empty] | 16.88 | [13 empty] | -
[11 empty] | 02.04.2026 | 25 dt. 17.04.2026 |  | 1: 7.14; 2: 5; 3: 28; 5: 12; 11: BDL(DL=02); 25: 50 |  |  |  | Complying | Complying |  | 7.29 | 145 | 508 |  | 380 | [5 empty] | 14.52 | [13 empty] | -
[11 empty] | 18.05.2026 | 278 dt. 29.05.2026 |  | 1: 7.03; 2: 7.2; 3: 44; 5: 13; 11: ND; 25: 70 |  |  |  | Complying | Complying |  | 7.6 | 98 | 320 |  | 186 | [5 empty] | 17.93 | [13 empty] | -
[11 empty] | 05.06.2026 | 441 dt. 16.06.2026 |  | 1: 7.63; 2: 8; 3: 44; 5: 17; 25: 80 |  |  |  | Complying | Complying |  | 7.6 | 130 | 428 |  | 186 | [19 empty] | -
| July, 2026 1st Phase | [9 empty] | 04.07.2026 | 597 dt.13.07.2026 | 127.53 | 1: 7.86; 2: 7.2; 3: 36; 5: 11; 25: 80; 52: BDL |  |  |  | Complying | Complying | 572 | 6.97 | 108 | 360 |  | 146 | [19 empty] | 1.25 X105 | [26 empty] | 20
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | 728 dt. 05.08.2026 |  | 1: 7.47; 2: 7.2; 3: 40; 5: 12; 6: 480; 7: 77.97; 9: 94.6; 12: ND; 13: 1.72; 14: ND; 16: ND; 17: ND; 18: 65.2; 19: 70; 20: 186; 23: 130; 24: 256; 25: 90; 28: 2.3; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: BDL(DL=0.264); 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: BDL(DL=02); 55: 880 |  |  |  | Complying | Complying |  | 7.08 | 520 | 1808 |  | 380 | 1032 | 95.97 |  | 409.78 |  |  | 23.94 | 28.96 | 3.24 |  | 9.6 | ND | 175.4 | 434 | 398 |  |  | 432 | 832 | 1.46 X105 |  |  | 5.48 |  |  | BDL(DL=0.001) | BDL(DL=0.230) | 3.293 | BDL(DL=0.07) | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | BDL(DL=0.5243) | BDL(DL=0.001) | [8 empty] | 26.5 |  |  | 1887
20 | (KRN-STP-016) 8 MLD STP Kambopura, Karnal by ULBD 31.10.2024
[11 empty] | 06.01.2026 | 4196 dt. 15.01.2026 | 52.17 | 1: 7.02; 2: 6.5; 3: 40; 5: 9; 11: ND |  |  |  | Complying | Complying | 25.58 | 6.78 | 120 | 396 |  | 128 | [5 empty] | 13.92
[11 empty] | 04.02.2026 | 4419 dt. 16.02.2026 |  | 1: 7.7; 2: 8.5; 3: 44; 5: 16; 11: ND; 25: 50 |  |  |  | Complying | Complying |  | 6.98 | 120 | 408 |  | 198 | [5 empty] | 16.38 | [13 empty] | -
[11 empty] | 09.03.2026 | 4675 dt. 24.03.2026 |  | 1: 7.4; 2: 5.6; 3: 36; 5: 12; 11: ND; 25: 50 |  |  |  | Complying | Complying |  | 7.15 | 130 | 424 |  | 164 | [5 empty] | 14.34 | [13 empty] | -
[11 empty] | 08.04.2026 | 87 dt. 24.04.2026 |  | 1: 7.44; 2: 6.8; 3: 40; 5: 14; 11: ND; 25: 70 |  |  |  | Complying | Complying |  | 6.93 | 102 | 340 |  | 205 | [5 empty] | 17.39 | [13 empty] | -
[11 empty] | 18.05.2026 | 277 dt. 29.05.2026 |  | 1: 7.94; 2: 6.8; 3: 36; 5: 11; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 7.8 | 102 | 352 |  | 178 | [5 empty] | 19.36 | [13 empty] | -
[11 empty] | 05.06.2026 | 440 dt. 16.06.2026 |  | 1: 7.94; 2: 5.2; 3: 36; 5: 10; 25: 80 |  |  |  | Complying | Complying |  | 7.6 | 110 | 368 |  | 126 | [19 empty] | -
| July, 2026 1st Phase | [9 empty] | 04.07.2026 | 601 dt. 13.07.2026 | 29.18 | 1: 7.6; 2: 7.5; 3: 36; 5: 13; 25: 60; 52: BDL |  |  |  | Complying | Complying | 57.67 | 7.09 | 120 | 392 |  | 192 | [19 empty] | 1.13X105 | [26 empty] | 22
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | 731 dt. 05.08.2026 |  | 1: 7.89; 2: 6; 3: 28; 5: 9; 6: 550; 7: 43.98; 9: 112.62; 12: ND; 13: ND; 14: ND; 16: ND; 17: ND; 18: 72.2; 19: 116; 20: 172; 23: 128; 24: 288; 25: 70; 28: 2.27; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: 0.725; 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: BDL(DL=02); 55: 1008 |  |  |  | Complying | Complying |  | 7.59 | 120 | 412 |  | 175 | 1020 | 61.98 |  | 312.68 |  |  | 21.94 | 14.98 | 2.84 |  | 4.6 | ND | 73.8 | 124 | 200 |  |  | 328 | 324 | 1.19X105 |  |  | 4.13 |  |  | BDL(DL=0.001) | BDL(DL=0.230) | 6.382 | BDL(DL=0.07) | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | BDL(DL=0.5243) | BDL(DL=0.001) | [8 empty] | 22 |  |  | 1870
21 | (KRN-STP-016) 2 MLD STP Village Kohand, Karnal by PHED 31.03.2025
[11 empty] | 09.01.2026 | 4274 dt. 21.01.2026 |  | 1: 7.87; 2: 3.8; 3: 20; 5: 6; 11: ND |  |  |  | Complying | Complying |  | 6.96 | 125 | 420 |  | 208 | [5 empty] | 13.68
[11 empty] | 17.02.2026 | 4531 dt. 02.03.2026 | 5700.7 | 1: 8.24; 2: 7.8; 3: 44; 5: 13; 11: ND; 25: 70 |  |  |  | Complying | Complying | 10184623 | 7.22 | 102 | 352 |  | 182 | [5 empty] | 13.92 | [13 empty] | -
[11 empty] | 17.03.2026 | 4754 dt. 24.03.2026 | 9228.2 | 1: 8.07; 2: 7.2; 3: 44; 5: 13; 11: ND; 25: 50 |  |  |  | Complying | Complying | 115588.661 | 8.18 | 112 | 380 |  | 208 | [5 empty] | 14.08 | [13 empty] | -
[11 empty] | 08.04.2026 | 90 dt. 24.04.2026 |  | 1: 7.03; 2: 7; 3: 32; 5: 11; 11: ND; 25: 70 |  |  |  | Complying | Complying |  | 7 | 110 | 380 |  | 126 | [5 empty] | 14.52 | [13 empty] | -
[11 empty] | 20.05.2026 | 304 dt. 29.05.2026 |  | 1: 8.07; 2: 7.8; 3: 48; 5: 13; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 8.32 | 240 | 864 |  | 252 | [5 empty] | 23.82 | [13 empty] | -
[11 empty] | 03.06.2026 | 410 dt. 15.06.2026 |  | 1: 7.86; 2: 5.2; 3: 28; 5: 9; 11: -; 25: 50 |  |  |  | Complying | Complying |  | …. | …. | …. |  | …. | [19 empty] | -
| July, 2026 1st Phase | [9 empty] | 02.07.2026 | 567 dt. 09.07.2026 | 137 | 1: 8.29; 2: 4.5; 3: 24; 5: 5; 25: ND |  |  |  | Complying | Complying | 174 | 7.48 | 120 | 380 |  | 173 | [19 empty] | 1.18X105 | [26 empty] | 25.5
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | 733 dt. 05.08.2026 |  | 1: 7.69; 2: 7; 3: 36; 5: 11; 6: 640; 7: 57.98; 9: 116.46; 12: ND; 13: 2.08; 14: ND; 16: ND; 17: ND; 18: 54; 19: 97.4; 20: 162.6; 23: 120; 24: 260; 25: 90; 28: 1.84; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: BDL(DL=0.264); 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: BDL(DL=02); 55: 1167 |  |  |  | Complying | Complying |  | 7.44 | 82 | 276 |  | 136 | 676 | 115.96 |  | 242.93 |  |  | 13.38 | 11.68 | 2.56 |  | 12.8 | ND | 162.8 | 434 | 200 |  |  | 388 | 370 | 1.26 X105 |  |  | 2.65 |  |  | BDL(DL=0.001) | BDL(DL=0.230) | BDL(DL=0.264) | BDL(DL=0.07) | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | BDL(DL=0.5243) | BDL(DL=0.001) | [8 empty] | 12.5 |  |  | 1230
Panipat
22 | (PNP-STP-001) 35 MLD STP Sewah, Panipat by PHED in March, 2000 (UASB Extended Aeration) | PHED | 10 | 7 to 8 | 100 | 20
[11 empty] | 06.01.2026 | 4187 dt. 15.01.2026 |  | 1: 7.08; 2: 6.2; 3: 40; 5: 11; 11: ND |  |  |  | Complying | Complying
[11 empty] | 10.02.2026 | 4479 dt. 24.02.2026 |  | 1: 8.12; 2: 7.5; 3: 40; 5: 16; 11: ND; 25: 60 |  |  |  | Complying | Complying
[11 empty] | 07.03.2026 | 4657 dt. 19.03.2026 | - | 1: 7.79; 2: 7.2; 3: 40; 5: 8; 11: ND; 25: 50 |  |  |  | Complying | Complying | 1200 | 7.9 | 160 | 476 |  | 200 | [5 empty] | 13.72 | [13 empty] | -
[11 empty] | 07.04.2026 | 77 dt. 23.04.2026 |  | 1: 7.34; 2: 6; 3: 36; 5: 9; 11: ND; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 06.05.2026 | 195 dt. 14.05.2026 |  | 1: 7.76; 2: 6.8; 3: 32; 5: 6; 11: ND; 25: ND |  |  |  | Complying | Complying
[11 empty] | 06.06.2026 | 454 dt. 16.06.2026 |  | 1: 7.97; 2: 6; 3: 32; 5: 9; 25: 50 |  |  |  | Complying | Complying
| July, 2026 1st Phase | [9 empty] | 04.07.2026 | 613 dt. 13.07.2026 |  | 1: 7.76; 2: 7.5; 3: 36; 5: 14; 25: 90; 52: BDL(DL=02); 55: 2019 |  |  |  | Complying | Complying
23 | (PNP-STP-002) 10 MLD STP Jattal Road, Panipat by PHED in March,. 2000 (UASB Extended Aeration) | PHED | 10 | 7 to 8 | 100 | 20
[11 empty] | 06.01.2026 | 4193 dt. 15.01.2026 |  | 1: 6.86; 2: 6.6; 3: 40; 5: 13; 11: ND |  |  |  | Complying | Complying
[11 empty] | 09.02.2026 | 4475 dt. 24.02.2026 |  | 1: 7.52; 2: 7.6; 3: 44; 5: 16; 11: 2.93; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 07.03.2026 | 4662 dt. 19.03.2026 |  | 1: 8.3; 2: 6.2; 3: 40; 5: 13; 11: ND; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 07.04.2026 | 73 dt. 23.04.2026 | - | 1: 7.29; 2: 5.8; 3: 28; 5: 9; 11: ND; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 07.05.2026 | 207 dt. 18.05.2026 |  | 1: 8.19; 2: 7.6; 3: 40; 5: 13; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 06.06.2026 | 456 dt. 16.06.2026 |  | 1: 7.78; 2: 7.6; 3: 40; 5: 11; 25: 50 |  |  |  | Complying | Complying
| July, 2026 1st Phase | [9 empty] | 04.07.2026 | 607 dt. 13.07.2026 |  | 1: 7.34; 2: 7.5; 3: 36; 5: 12; 25: 60; 52: BDL(DL=02); 55: 1453 |  |  |  | Complying | Complying
24 | (PNP-STP-003) 5 MLD STP Samalkha, Panipat by PHED in June, 2013 (MBBR) | PHED | 30 | 7 to 8 | 100 | 50 | [68 empty] | 7.6 | 54 | 236 |  | 166 | [5 empty] | 11.16 |  |  | 0.39
[11 empty] | 08.01.2026 | 4233 dt. 20.01.2026 |  | 1: 7.32; 2: 6.8; 3: 44; 5: 12; 11: ND |  |  |  | Complying | Complying |  | 6.94 | 120 | 408 |  | 224 | [5 empty] | 14.48
[11 empty] | 10.02.2026 | 4474 dt. 23.02.2026 |  | 1: 8.02; 2: 8; 3: 48; 5: 17; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 7.62 | 92 | 320 |  | 176 | [5 empty] | - | [13 empty] | -
[11 empty] | 07.03.2026 | 4653 dt. 19.03.2026 |  | 1: 7.6; 2: 7.2; 3: 40; 5: 9; 11: ND; 25: 70 |  |  |  | Complying | Complying |  | 7.88 | 170 | 480 |  | 142 | [5 empty] | 14.73 | [13 empty] | -
| By Pass | [9 empty] | 12.03.2026 | 4702 dt. 25.03.2026 |  | 1: 7.9; 2: 84; 3: 252; 5: 184; 11: 19.48; 25: 2200 |  |  |  | Non Complying | Non Complying
[11 empty] | 08.04.2026 | 75 dt. 23.04.2026 |  | 1: 7.03; 2: 5.8; 3: 40; 5: 14; 11: ND; 25: 60 |  |  |  | Complying | Complying |  | 6.96 | 135 | 480 |  | 348 | [5 empty] | 13.28 | [13 empty] | -
| May, 2026 | [9 empty] | 05.05.2026 | 117 dt. 13.05.2026 |  | 1: 8.18; 2: 12; 3: 56; 5: 16 |  |  |  | Non Complying | Non Complying |  | 8.08 | 92 | 296 |  | 125
[11 empty] | 09.06.2026 | 474 dt. 22.06.2026 |  | 1: 8.17; 2: 9.2; 3: 48; 5: 19 |  |  |  | Complying | Complying
[11 empty] | 04.07.2026 | 611 dt. 13.07.2026 |  | 1: 7.29; 2: 14; 3: 88; 5: 25; 25: 800; 52: BDL(DL=02); 55: 1126 |  |  |  | Non Complying | Non Complying
25 | (PNP-STP-004) 25 MLD STP Sewah, Panipat by PHED in April, 2016 (SBR) | PHED | 10 | 7 to 8 | 100 | 20
[11 empty] | 06.01.2026 | 4188 dt. 15.01.2026 |  | 1: 6.88; 2: 6.5; 3: 44; 5: 12; 11: ND |  |  |  | Complying | Complying
[11 empty] | 10.02.2026 | 4480 dt. 24.02.2026 |  | 1: 7.88; 2: 6; 3: 36; 5: 13; 11: ND |  |  |  | Complying | Complying
[11 empty] | 07.03.2026 | 4658 dt. 19.03.2026 |  | 1: 7.69; 2: 7.4; 3: 44; 5: 8; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 7.95 | 130 | 396 |  | 233 | [5 empty] | 14.38 | [13 empty] | -
[11 empty] | 07.04.2026 | 76 dt. 23.04.2026 |  | 1: 7.01; 2: 5.2; 3: 32; 5: 8; 11: ND; 25: 70 |  |  |  | Complying | Complying
| May, 2026 | [9 empty] | 06.05.2026 | 194 dt. 14.05.2026 |  | 1: 7.94; 2: 5; 3: 24; 5: 7; 11: ND; 25: 50 |  |  |  | Complying | Complying
| June, 2026 | [9 empty] | 06.06.2026 | 453 dt. 16.06.2026 |  | 1: 7.75; 2: 8.2; 3: 44; 5: 12; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 04.07.2026 | 612 dt. 13.07.2026 |  | 1: 7.12; 2: 8.2; 3: 40; 5: 13; 25: 80; 52: BDL(DL=02); 55: 2126 |  |  |  | Complying | Complying
26 | (PNP-STP-005) 20 MLD STP Jattal Road, Panipat by PHED in April, 2016 (SBR) | PHED | 10 | 7 to 8 | 100 | 20 | [68 empty] | 7.53 | 140 | 548 |  | 179 | [5 empty] | 12.64 |  |  | 0.35
[11 empty] | 06.01.2026 | 4194 dt. 15.01.2026 |  | 1: 6.78; 2: 6.2; 3: 36; 5: 12; 11: ND |  |  |  | Complying | Complying
[11 empty] | 09.02.2026 | 4475-A dt. 24.02.2026 |  | 1: 8.03; 2: 7.8; 3: 48; 5: 18; 11: 3.08; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 07.03.2026 | 4660 dt. 19.03.2026 |  | 1: 8.49; 2: 4.8; 3: 24; 5: 7; 11: ND; 25: ND |  |  |  | Complying | Complying |  | 7.37 | 110 | 360 |  | 166 | [5 empty] | 13.08 | [13 empty] | -
[11 empty] | 07.04.2026 | 71 dt. 23.04.2026 |  | 1: 7.36; 2: 6.4; 3: 44; 5: 13; 11: ND; 25: 80 |  |  |  | Complying | Complying
| May, 2026 | [9 empty] | 07.05.2026 | 208 dt 18.05.2026 |  | 1: 8.3; 2: 7.4; 3: 36; 5: 11; 11: ND; 25: 80 |  |  |  | Complying | Complying
| June, 2026 | [9 empty] | 06.06.2026 | 455 dt. 16.06.2026 |  | 1: 7.98; 2: 8.2; 3: 48; 5: 17; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 04.07.2026 | 606 dt. 13.07.2026 |  | 1: 7.48; 2: 7.2; 3: 40; 5: 9; 25: 50; 52: BDL(DL=02); 55: 1432 |  |  |  | Complying | Complying
27 | (PNP-STP-006) 30 MLD, STP, Sector-19 by HSVP, Panipat 1.11.2018 (SBR) | HSVP | <5 | 5.5 to 9 | <100 | <10 | <5 | <10 | <2 | <100 MPN/ 100 ml | [74 empty] | 15.88 |  |  | 0.33
[11 empty] | 06.01.2026 | 4191 dt. 15.01.2026 | 307151119 | 1: 6.78; 2: 6.5; 3: 44; 5: 12; 11: ND |  |  |  | Complying | Complying
[11 empty] | 10.02.2026 | 4481 dt. 24.02.2026 |  | 1: 7.96; 2: 6; 3: 28; 5: 11; 11: 1.43; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 07.03.2026 | 4656 dt. 19.03.2026 |  | 1: 8.69; 2: 8.4; 3: 44; 5: 7; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 7.29 | 150 | 424 |  | 160 | [5 empty] | 14.32 | [13 empty] | -
[11 empty] | 07.04.2026 | 74 dt. 23.04.2026 | 31755803 | 1: 7.17; 2: 5.6; 3: 32; 5: 11; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 07.05.2026 | 205 dt. 18.05.2026 |  | 1: 6.4; 2: 6.5; 3: 40; 5: 14; 11: ND; 25: 80 |  |  |  | Complying | Complying
| June, 2026 | [9 empty] | 16.06.2026 | 449 dt. 16.06.2026 | 151.8 | 1: 6.9; 2: 6.2; 3: 36; 5: 11; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 04.07.2026 | 610 dt. 13.07.2026 |  | 1: 7.48; 2: 7.8; 3: 44; 5: 12; 25: 90; 52: BDL(DL=02); 55: 1065 |  |  |  | Complying | Complying
28 | (PNP-STP-007) 0.8 MLD STP, Sector-6 by HSVP, Panipat 30.04.2019 (SBR) | HSVP | 5 | 5.5-9 | 50 | 10 | 5 | 10 | 2 | [65 empty] | 7.53 | 130 | 600 |  | 252 | [5 empty] | 12.6 |  |  | 0.32
[11 empty] | 06.01.2026 | 4189 dt. 15.01.2026 | 496471 | 1: 7.12; 2: 6.2; 3: 36; 5: 13; 11: ND |  |  |  | Complying | Complying
[11 empty] | 09.02.2026 | 4477 dt. 24.02.2026 | 504318.799 | 1: 8.04; 2: 16; 3: 80; 5: 28; 11: 9.08; 25: 400 |  |  |  | Non Complying | Non Complying
[11 empty] | 07.03.2026 | 4655 dt. 19.03.2026 | 10 | 1: 8.02; 2: 9; 3: 48; 5: 12; 11: ND; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 07.04.2026 | 72 dt. 23.04.2026 | 515679.786 | 1: 7.03; 2: 6.8; 3: 44; 5: 12; 11: 3.42; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 07.05.2026 | 209 dt. 18.05.2026 |  | 1: 7.86; 2: 5.6; 3: 32; 5: 11; 11: ND; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 06.06.2026 | 450 dt. 16.06.2026 | 527857.1 | 1: 7.82; 2: 11.2; 3: 56; 5: 14; 25: 90 |  |  |  | Complying | Complying
29 | (PNP-STP-008) 15 MLD STP, Dev Colony, Panipat by ULBD 31.07.2023
[11 empty] | 06.01.2026 | 4190 dt. 15.01.2026 |  | 1: 7.23; 2: 14; 3: 72; 5: 23; 11: 7.28 |  |  |  | Non-Complying | Non-Complying
[11 empty] | 09.02.2026 | 4478 dt. 24.02.2026 | 1484611.034 | 1: 8.14; 2: 7.2; 3: 48; 5: 17; 11: 4.86; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 07.03.2026 | 4661 dt. 19.03.2026 | 854 | 1: 8.19; 2: 6.4; 3: 36; 5: 10; 11: ND; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 07.04.2026 | 69 dt. 23.04.2026 | 1721919.36 | 1: 7.15; 2: 5.8; 3: 32; 5: 8; 11: ND; 25: 60 |  |  |  | Complying | Complying
[11 empty] | 07.05.2026 | 204 dt. 18.05.2026 |  | 1: 8.07; 2: 6; 3: 32; 5: 8; 11: ND; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 06.06.2026 | 451 dt. 16.06.2026 |  | 1: 7.9; 2: 9.2; 3: 48; 5: 15; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 04.07.2026 | 608 dt. 13.07.2026 |  | 1: 7.16; 2: 5.8; 3: 20; 5: 9; 25: 60; 52: BDL(DL=02); 55: 608 |  |  |  | Complying | Complying
30 | (PNP-STP-009) 25 MLD STP, Barasat Road, Panipat by ULBD 31.12.2023
[11 empty] | 06.01.2026 | 4192 dt. 15.01.2026 | 766263 | 1: 6.79; 2: 7; 3: 40; 5: 11; 11: ND |  |  |  | Complying | Complying
[11 empty] | 09.02.2026 | 4476 dt. 24.02.2026 |  | 1: 7.92; 2: 8; 3: 44; 5: 17 |  |  |  | Complying | Complying
[11 empty] | 07.03.2026 | 4663 dt. 19.03.2026 | 25.5 | 1: 8.47; 2: 7; 3: 44; 5: 9; 11: ND; 25: 80 |  |  |  | Complying | Complying | 1599 | 7.99 | 160 | 484 |  | 366 | [5 empty] | 13.94 | [13 empty] | -
[11 empty] | 07.04.2026 | 70 dt. 23.04.2026 |  | 1: 7.07; 2: 7.8; 3: 40; 5: 15; 11: 2.64; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 07.05.2026 | 206 dt. 18.05.2026 |  | 1: 7.56; 2: 5.4; 3: 28; 5: 7; 11: ND; 25: ND |  |  |  | Complying | Complying
[11 empty] | 06.06.2026 | 448 dt. 16.06.2026 | 25.9 | 1: 7.69; 2: 8.2; 3: 44; 5: 13; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 04.07.2026 | 609 dt. 13.07.2026 |  | 1: 8.07; 2: 7.2; 3: 40; 5: 11; 25: 80; 52: BDL(DL=02); 55: 816 |  |  |  | Complying | Complying
31 | (PNP-STP-010) 3 MLD STP, Village Sewah, Panipat by PHED, Sept., 2023
[11 empty] | 08.01.2026 | 4232 dt. 20.01.2026 | 120 | 1: 7.42; 2: 5.8; 3: 36; 5: 9; 11: ND |  |  |  | Complying | Complying
[11 empty] | 10.02.2026 | 4482 dt. 24.02.2026 | 907 | 1: 7.96; 2: 7.5; 3: 44; 5: 13; 11: 2.48; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 07.04.2026 | 78 dt. 23.04.2026 | 150 | 1: 7.7; 2: 7.4; 3: 44; 5: 13; 11: 1.84; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 14.05.2026 | 196 dt. 14.05.2026 | 236 | 1: 8.04; 2: 7.2; 3: 36; 5: 11; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 16.06.2026 | 452 dt. 16.06.2026 |  | 1: 7.97; 2: 14; 3: 64; 5: 23; 25: 200 |  |  |  | Non-Complying | Non-Complying
[11 empty] | 04.07.2026 | 614 dt. 13.07.2026 | 1006 | 1: 7.52; 2: 6.8; 3: 36; 5: 12; 25: 70; 52: BDL(DL=02); 55: 1089 |  |  |  | Complying | Complying
32 | 3 MLD STP, Madlauda, PHED, Panipat 2026
Sonepat
33 | (SNP-STP-001) 30 MLD STP Rathdana Road , Sonepat by ULBD in 2003 (UASB)
[11 empty] | 06.01.2026 | 1897 dt. 15.01.2026 |  | 1: 7.42; 2: 9.2; 3: 48; 5: 17; 11: 7.84; 25: 63 |  |  |  | Complying | Complying |  | 7.46 | 170 | 744 |  | 280 | [5 empty] | 68.24 | [13 empty] | 9300
[11 empty] | 17.02.2026 | 2289, dt. 17.02.2026 |  | 1: 7.13; 2: 8.2; 3: 43.6; 5: 18; 11: 9.76; 25: 93 |  |  |  | Complying | Complying |  | 7.88 | 92 | 380.9 |  | 260 | [5 empty] | 28.02 | [13 empty] | 7000
[11 empty] | 06.03.2026 | 2534, dt. 16.03.2026 |  | 1: 7.54; 2: 7.2; 3: 32; 5: 14; 11: 8.28; 25: 79 |  |  |  | Complying | Complying |  | 7.92 | 94 | 376 |  | 240 | [5 empty] | 30.82 | [13 empty] | 8400
[11 empty] | 13.04.2026 | 113, dt. 23.04.2026 |  | 1: 8.41; 2: 8.2; 3: 48.3; 5: 17; 11: 8.54; 25: 93 |  |  |  | Complying | Complying |  | 8.58 | 88 | 322.5 |  | 205 | [5 empty] | 34.12 | [13 empty] | 7900
[11 empty] | 21.05.2026 | 314, dt. 29.05.2026 |  | 1: 8.8; 2: 7.2; 3: 36; 5: 7; 11: 9.56; 25: 93 |  |  |  | Complying | Complying |  | 8.78 | 130 | 528 |  | 325 | [5 empty] | 34.76 | [13 empty] | 11000
[11 empty] | 05.06.2026 | 419, dt. 18.06.2026 |  | 1: 9.11; 2: 8.2; 3: 40; 5: 17; 11: 9.33; 25: 84 |  |  |  | Complying | Complying |  | 8.24 | 105 | 416 |  | 240 | [5 empty] | 21.84 | [13 empty] | 9300
[11 empty] | 09.07.2026 | 339 M dt. 17.07.2026 |  | 1: 7.79; 2: 7.4; 3: 32; 5: 5; 6: 480; 11: 8.12; 12: 3.68; 25: 93; 52: BDL*(DL**=4); 55: 930 |  |  |  | Complying | Complying |  | 8.89 | 115 | 448 |  | 275 | 1470 |  |  |  |  | 24.66 | 8.1 | [12 empty] | 7000 | [26 empty] | 6.8
| July, 2nd phase 2026 | [9 empty] | 22.07.2026 | 379 M dt. 30.07.2026 |  | 7.94 | 8.2 | 40 |  | 19 | 3210 | 2708.9 | 580 | 116 | 1.29 | 10.73 | 2.65 | 3.4 |  | BDL*(DL**=0.4) | ND |  | 2107.532 | 60.764 | 30.515 |  |  | 580 | 360 | 49 |  |  | 50.74 |  |  | 0.174 | 0.006 | 0.094 | 0.125 | BDL*(DL**=0.0002) | BDL*(DL**=0.0005) | BDL*(DL**=0.001) | BDL*(DL**=0.001) | BDL*(DL**=0.0001) | BDL*(DL**=0.0002) | BDL*(DL**=0.0003 | 0.109 | BDL*(DL**=0.001) | 0.054 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.034 | BDL*(DL**=0.0006) | BDL*(DL**=4) |  |  | 5830 |  |  |  | Complying | Complying |  | 7.25 | 130 | 488 |  | 320 | 790 | 304.8 | 85 | 243 | 3.68 | 21.69 | 7.18 | 3.1 |  | 2.24 | 1.2 |  | 213.984 | 49.761 | 73.752 |  |  | 425 | 560 | 8400 |  |  | 4.72 |  |  | 0.256 | 0.112 | 0.094 | 0.125 | BDL*(DL**=0.0002) | BDL*(DL**=0.0005) | BDL*(DL**=0.001) | BDL*(DL**=0.001) | BDL*(DL**=0.0001) | BDL*(DL**=0.0002) | BDL*(DL**=0.0003) | 0.341 | BDL*(DL**=0.001) | 12.939 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.273 | BDL*(DL**=0.0006) | 7.8 |  |  | 1430
[11 empty] | 10.08.2026 | 668 M dt. 18.08.2026 |  | 7.96 | 8.6 | 48 |  | 18 | 1490 | 949.2 | 20 | 102 | 0.58 | 7.28 | 1.24 | 2.6 |  | 0.94 | ND |  | 1602.263 | 57.5 | 94.9 |  |  | 340 | 480 | 38 |  |  | 32.03 |  |  | 0.153 | 0.007 | 0.073 | 0.214 | 0.002 | 0.002 | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.021 | 0.123 | BDL*(DL**=0.001) | 0.037 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.035 | BDL*(DL**=0.0006) | BDL*(DL**=4) |  |  | 2690 |  |  |  | Complying | Complying |  | 6.85 | 180 | 544 |  | 340 | 950 | 833.4 | 350 | 112 | 2.78 | 29.56 | 6.24 | 11.4 |  | 4.8 | 2.4 |  | 179.314 | 38.3 | 63.3 |  |  | 450 | 320 | 9300 |  |  | 4.38 |  |  | 0.029 | BDL*(DL**=0.0016) | 2.66 | 0.169 | 0.012 | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.007) | BDL*(DL**=0.0145) | 0.223 | BDL*(DL**=0.001) | 2.421 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.226 | BDL*(DL**=0.0006) | 9.6 |  |  | 1750
34 | (SNP-STP-002) 25 MLD STP Kakrai Road, Sonepat by ULBD in March dt. 2018 (SBR)
[11 empty] | 06.01.2026 | 1895 dt. 15.01.2026 |  | 1: 7.13; 2: 6.8; 3: 36; 5: 14; 11: 6.14; 25: 58 |  |  |  | Complying | Complying |  | 7.49 | 75 | 304 |  | 260 | [5 empty] | 28.02 | [13 empty] | 7000
[11 empty] | 09.02.2026 | 2290, dt. 17.02.2026 |  | 1: 7.19; 2: 7.8; 3: 39.6; 5: 17; 11: 7.24; 25: 79 |  |  |  | Complying | Complying |  | 8.05 | 90 | 372.9 |  | 275 | [5 empty] | 38.02 | [13 empty] | 6300
[11 empty] | 06.03.2026 | 2537, dt. 16.03.2026 |  | 1: 7.17; 2: 6.4; 3: 32; 5: 15; 11: 8.12; 25: 84 |  |  |  | Complying | Complying |  | 7.48 | 104 | 424 |  | 285 | [5 empty] | 33.84 | [13 empty] | 9300
[11 empty] | 13.04.2026 | 111, dt. 23.04.2026 | 20 | 1: 8.52; 2: 7.2; 3: 40.3; 5: 14; 11: 9.84; 25: 79 |  |  |  | Complying | Complying |  | 8.14 | 112 | 451.5 |  | 290 | [5 empty] | 39.76 | [13 empty] | 8400
[11 empty] | 21.05.2026 | 313, dt. 29.05.2026 |  | 1: 7.21; 2: 8.8; 3: 44; 5: 9; 11: 9.68; 25: 93 |  |  |  | Complying | Complying |  | 8.2 | 125 | 480 |  | 345 | [5 empty] | 42.72 | [13 empty] | 7000
[11 empty] | 05.06.2026 | 420, dt. 18.06.2026 |  | 1: 7.53; 2: 9.2; 3: 48; 5: 16; 11: 11.4; 25: 93 |  |  |  | Complying | Complying |  | 7.02 | 94 | 392 |  | 1020 | [5 empty] | 32.12 | [13 empty] | 7000
[11 empty] | 09.07.2026 | 340 M dt. 17.07.2026 |  | 1: 7.62; 2: 5.6; 3: 40; 5: 8; 6: 450; 9: 56; 11: 6.84; 12: 2.12; 17: ND; 25: 63; 52: BDL*(DL**=4); 55: 610 |  |  |  | Complying | Complying |  | 7.13 | 104 | 408 |  | 310 | 1180 |  |  | 284 |  | 24.42 | 13.16 |  |  |  |  | 0.75 | [7 empty] | 8400 | [26 empty] | 7.4 |  |  | 2150
| July, 2nd phase 2026 | [9 empty] | 22.07.2026 | 377 M dt. 30.07.2026 |  | 7.77 | 4.6 | 28 |  | 16 | 1340 | 492.3 | 160 | 188 | 0.26 | 5.92 | BDL*(DL**=0.5) | 4.2 |  | 2.22 | ND |  | 363.41 | 103.455 | 257.994 |  |  | 160 | 570 | 84 |  |  | 4.83 |  |  | 0.134 | BDL*(DL**=0.0004) | 0.035 | 0.073 | BDL*(DL**=0.0002) | BDL*(DL**=0.0005) | BDL*(DL**=0.001) | BDL*(DL**=0.001) | BDL*(DL**=0.0001) | BDL*(DL**=0.0002) | BDL*(DL**=0.0003 | 0.524 | BDL*(DL**=0.001) | 0.078 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.029 | BDL*(DL**=0.0006) | BDL*(DL**=4) |  |  | 2430 |  |  |  | Complying | Complying |  | 7 | 85 | 272 |  | 240 | 820 | 324.8 | 210 | 147 | 1.76 | 29.34 | 2.17 | 3.6 |  | 4.54 | 1.8 |  | 223.318 | 43.435 | 81.509 |  |  | 210 | 520 | 7000 |  |  | 4.97 |  |  | 0.103 | BDL*(DL**=0.0004) | 0.035 | 0.073 | BDL*(DL**=0.0002) | BDL*(DL**=0.0005) | BDL*(DL**=0.001) | BDL*(DL**=0.001) | BDL*(DL**=0.0001) | BDL*(DL**=0.0002) | BDL*(DL**=0.0003) | 0.359 | BDL*(DL**=0.001) | 0.078 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.029 | BDL*(DL**=0.0006) |  |  |  | 1490
[11 empty] | 10.08.2026 | 669 M dt. 18.08.2026 |  | 6.69 | 5.4 | 32 |  | 15 | 1750 | 587.2 | 280 | 178 | 0.51 | 8.42 | 0.74 | 2.6 |  | 1.24 | ND |  | 400.03 | 77.2 | 127.4 |  |  | 300 | 640 | 70 |  |  | 4.88 |  |  | 0.022 | BDL*(DL**=0.0016) | 0.173 | 0.134 | BDL*(DL**=0.0008) | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | BDL*(DL**=0.0145) | BDL*(DL**=0.0009) | BDL*(DL**=0.001) | 0.021 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.027 | BDL*(DL**=0.0006) | BDL*(DL**=4) |  |  | 3180 |  |  |  | Complying | Complying |  | 7.24 | 92 | 336 |  | 295 | 1890 | 624.8 | 320 | 210 | 1.45 | 29.24 | 6.44 | 12.2 |  | 3.56 | 1.6 |  | 409.032 | 82.3 | 135.8 |  |  | 380 | 680 | 5800 |  |  | 6.83 |  |  | BDL*(DL**=0.0024) | BDL*(DL**=0.0016) | 7.385 | 0.259 | 0.134 | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.007) | 0.03 | 0.216 | BDL*(DL**=0.001) | 7.959 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.119 | BDL*(DL**=0.0006) | 6.6 |  |  | 3360
35 | (SNP-STP-003) 7.5 MLD Sonepat Rajiv Gandhi Edu. City Phase.I dt. Sonepat by HSVP (ASP) |  | <10 | 7-8 | Nil | <10 |  |  |  | 200 | [64 empty] | 7.48 | 38 | 164 |  | 118 | [5 empty] | 11.05 |  |  | 0.22
[11 empty] | 29.01.2026 | 2200 dt. 09.02.2026 |  | 1: 7.62; 2: 6.4; 3: 36.2; 5: 15; 11: 8; 25: 77 |  |  |  | Complying | Complying |  | 7.91 | 85 | 354.8 |  | 230 | [5 empty] | 30.82 | [13 empty] | 3900
[11 empty] | 10.02.2026 | 2293, dt. 17.02.2026 |  | 1: 7.86; 2: 6.2; 3: 47.6; 5: 16; 11: 7.12; 25: 49 |  |  |  | Complying | Complying |  | 8.09 | 110 | 436.4 |  | 270 | [5 empty] | 31.56 | [13 empty] | 8400
[11 empty] | 25.03.2026 | 2677, dt. 03.04.2026 |  | 1: 6.9; 2: 5.8; 3: 32; 5: 12; 11: 7.92; 25: 63 |  |  |  | Complying | Complying |  | 8.23 | 85 | 336 |  | 220 | [5 empty] | 34.72 | [13 empty] | 7000
[11 empty] | 13.04.2026 | 109, dt. 23.04.2026 |  | 1: 7.2; 2: 8.6; 3: 44.3; 5: 16; 11: 8.44; 25: 93 |  |  |  | Complying | Complying |  | 8.24 | 102 | 393.9 |  | 255 | [5 empty] | 37.12 | [13 empty] | 8000
[11 empty] | 29.05.2026 | 272, dt. 29.05.2026 |  | 1: 7.88; 2: 8.6; 3: 48; 5: 15; 11: 8.406 |  |  |  | Complying | Complying |  | 7.98 | 44 | 152 |  | 98 | [5 empty] | 19.614
[11 empty] | 09.06.2026 | 198, dt. 15.06.2026 |  | 1: 7.25; 2: 6.2; 3: 32; 5: 13; 11: 6.42; 25: 58 |  |  |  | Complying | Complying |  | 7.96 | 110 | 416 |  | 270 | [5 empty] | 28.12 | [13 empty] | 6300
[11 empty] | 03.07.2026 | 273 M dt. 10.07.2026 |  | 1: 7.18; 2: 5.4; 3: 28; 5: 7.2; 6: 480; 9: 164; 11: 5.24; 12: BDL(DL=0.5); 17: ND; 25: 63; 32: BDL(DL=0.006); 52: BDL*(DL**=4); 55: 940 |  |  |  | Complying | Complying |  | 7.12 | 125 | 448 |  | 235 | 2780 |  |  | 480 |  | 31.64 | 8.14 |  |  |  |  | ND | [7 empty] | 7900 | [6 empty] | 0.019 | [19 empty] | 7.2 |  |  | 5060
| July, 2nd phase 2026 | [9 empty] | 17.07.2026 | 351 M dt. 27.07.2026 | 1 | 7.56 | 8.2 | 44 | BDL*(DL**=4) | 9 | 320 | 171.2 | 150 | 104 | 0.25 | 1.25 | BDL(DL=0.5) | 6.4 |  | 0.26 | ND |  | 153.458 | 64.885 | 45.868 |  |  | 250 | 400 | 63 |  |  | 3.42 |  |  | 0.197 | BDL*(DL**=0.006) | 0.047 | 0.011 | BDL*(DL**=0.007) | BDL*(DL**=0.015) | BDL*(DL**=0.04) | BDL*(DL**=0.05) | BDL*(DL**=0.004) | BDL*(DL**=0.007) | 0.011 | BDL*(DL**=0.002) | BDL*(DL**=0.01) | BDL*(DL**=0.04) |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.075) |  | 0.12 | BDL*(DL**=0.007) |  |  |  | 580 |  |  |  | Complying | Complying | - | 7.42 | 95 | 296 | 6.4 | 280 | 890 | 424.8 | 350 | 101 | 0.78 | 8.11 | 3.67 | 1.2 |  | 0.29 | 2.8 |  | 430.576 | 83.649 | 69.114 |  |  | 790 | 555 | 7000 |  |  | 8.24 |  |  | 0.319 | BDL*(DL**=0.006) | 1.88 | 0.116 | BDL*(DL**=0.007) | 0.023 | BDL*(DL**=0.04) | BDL*(DL**=0.05) | BDL*(DL**=0.004) | BDL*(DL**=0.007) | 0.006 | BDL*(DL**=0.002) | BDL*(DL**=0.01) | BDL*(DL**=0.04) |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.075) |  | 0.057 | BDL*(DL**=0.007) |  |  |  | 1620
[11 empty] | 06.08.2026 | 651 M dt. 14.08.2026 |  | 7.32 | 4.8 | 28 | BDL*(DL**=4) | 14 | 1160 | 249.9 | 340 | 135 | 0.32 | 3.91 | BDL*(DL**=0.5) | 1.7 |  | BDL*(DL**=0.4) | ND |  | 310.564 | 45.4 | 74.9 |  |  | 455 | 380 | 58 |  |  | 6.98 |  |  | 0.053 | 0.003 | BDL*(DL**=0.0005) | 0.003 | BDL*(DL**=0.0008) | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.024 | BDL*(DL**=0.0009) | BDL*(DL**=0.001) | BDL*(DL**=0.001) |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.035 | BDL*(DL**=0.0006) |  |  |  | 2110 |  |  |  | Complying | Complying |  | 7.44 | 102 | 424 | 9.2 | 235 | 1350 | 313.7 | 680 | 142 | 1.05 | 19.24 | 4.12 | 7.8 |  | 0.92 | 1.6 |  | 348.259 | 53.9 | 88.9 |  |  | 680 | 450 | 7900 |  |  | 7.19 |  |  | 0.127 | 0.013 | 1.745 | 0.245 | 0.009 | 0.029 | 0.16 | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.007) | 0.105 | BDL*(DL**=0.0009) | BDL*(DL**=0.001) | 0.985 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.061 | BDL*(DL**=0.0006) |  |  |  | 2460
36 | (SNP-STP-004) 4.5 MLD STP Kharkhoda Sonepat by PHED 1.8.2013 (MBBR) |  | 30 | 7.0-8.5 | 100 | 40
[11 empty] | 29.01.2026 | 2199 dt. 09.02.2026 |  | 1: 7.92; 2: 7.8; 3: 48.3; 5: 15; 11: 8.4; 25: 70 |  |  |  | Complying | Complying |  | 7.28 | 102 | 419.3 |  | 228 | [5 empty] | 39.16 | [13 empty] | 6300
[11 empty] | 10.02.2026 | 2295, dt. 17.02.2026 |  | 1: 7.26; 2: 6.2; 3: 39.6; 5: 17; 11: 6.84; 25: 58 |  |  |  | Complying | Complying |  | 7.19 | 90 | 357.1 |  | 255 | [5 empty] | 40.28 | [13 empty] | 8400
[11 empty] | 25.03.2026 | 2678, dt. 03.04.2026 |  | 1: 7.73; 2: 7.4; 3: 48; 5: 13; 11: 8.22; 25: 84 |  |  |  | Complying | Complying |  | 7.24 | 92 | 376 |  | 270 | [5 empty] | 46.44 | [13 empty] | 9300
[11 empty] | 13.04.2026 | 115, dt. 23.04.2026 |  | 1: 7.94; 2: 8.2; 3: 36.2; 5: 18; 11: 7.24; 25: 93 |  |  |  | Complying | Complying |  | 7.81 | 102 | 395.1 |  | 255 | [5 empty] | 50.26 | [13 empty] | 5800
[11 empty] | 27.05.2026 | 355, dt. 04.06.2026 |  | 1: 7.94; 2: 6.2; 3: 28; 5: 12; 11: 6.02; 25: 49 |  |  |  | Complying | Complying |  | 7.79 | 95 | 344 |  | 290 | [5 empty] | 41.84 | [13 empty] | 7000
[11 empty] | 08.06.2026 | 197, dt. 15.06.2026 |  | 1: 8.33; 2: 12; 3: 64; 5: 17; 11: 9.48; 25: 93 |  |  |  | Non-Complying | Non-Complying |  | 7.76 | 102 | 392 |  | 275 | [5 empty] | 37.12 | [13 empty] | 7900
[11 empty] | 03.07.2026 | 274 M dt. 10.07.2026 |  | 1: 7.39; 2: 5.8; 3: 32; 5: 26; 6: 750; 9: 127; 11: 4.64; 12: 0.77; 25: 79; 52: BDL*(DL**=4); 55: 1370 |  |  |  | Complying | Complying |  | 7.84 | 110 | 408 |  | 280 | 1540 |  |  | 258 |  | 24.16 | 7.14 | [12 empty] | 9300 | [26 empty] | 7.4 |  |  | 2790
| July, 2nd phase 2026 | [9 empty] | 20.07.2026 | 359 M dt. 29.07.2026 |  | 7.28 | 12 | 68 | BDL*(DL**=4) | 25 | 1240 | 484.8 | 350 | 133 | 0.76 | 7.13 | 0.82 | 3.4 |  | 0.46 | ND |  | 285.868 | 113.084 | 87.37 |  |  | 500 | 750 | 70 |  |  | 4.75 |  |  | 0.127 | BDL*(DL**=0.0004) | 0.13 | 0.094 | BDL*(DL**=0.0002) | BDL*(DL**=0.005) | BDL*(DL**=0.001) | BDL*(DL**=0.00006) | BDL*(DL**=0.00001) | BDL*(DL**=0.00002) | BDL*(DL**=0.00003) | 0.104 | BDL*(DL**=0.001) | 0.05 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.047 | BDL*(DL**=0.00006) |  |  |  | 2260 |  |  |  | Non-Complying | Non-Complying |  | 7.07 | 102 | 344 | 6.4 | 205 | 1150 | 409.8 | 420 | 121 | 1.05 | 24.16 | 2.79 | 2.8 |  | 1.78 | 2.4 |  | 231.141 | 99.556 | 111.841 |  |  | 600 | 575 | 8400 |  |  | 3.83 |  |  | 0.311 | BDL*(DL**=0.0004) | 23.897 | 0.446 | 0.024 | 0.025 | 0.04 | BDL*(DL**=0.00006) | BDL*(DL**=0.00001) | BDL*(DL**=0.00002) | 0.052 | 0.254 | BDL*(DL**=0.001) | 21.953 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.047 | BDL*(DL**=0.00006) |  |  |  | 2260
[11 empty] | 06.08.2026 | 652 M dt. 14.08.2026 |  | 7.52 | 16 | 92 |  | 35 | 1740 | 297.4 | 140 | 146 | 0.58 | 8.02 | 2.47 | 2.4 |  | 0.92 | ND |  | 310.461 | 69.9 | 115.4 |  |  | 150 | 580 | 130 |  |  | 5.6 |  |  | 0.053 | 0.003 | 0.108 | 0.003 | 0.001 | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | 0.001 | BDL*(DL**=0.0007) | BDL*(DL**=0.0145) | BDL*(DL**=0.0009) | BDL*(DL**=0.001) | 0.012 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.035 | BDL*(DL**=0.0006) | BDL*(DL**=4) |  |  | 3160 |  |  |  | Non-Complying | Non-Complying |  | 7.25 | 155 | 472 |  | 315 | 1910 | 374.8 | 300 | 155 | 1.33 | 28.12 | 8.44 | 9.2 |  | 2.16 | 3.2 |  | 345.108 | 126.3 | 208.4 |  |  | 310 | 1050 | 6300 |  |  | 6.65 |  |  | 0.204 | 0.008 | 16.406 | 0.225 | 0.008 | 0.011 | 0.009 | BDL*(DL**=0.001) | 0.004 | BDL*(DL**=0.0007) | 0.153 | 0.726 | BDL*(DL**=0.001) | 9.158 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.109 | BDL*(DL**=0.0006) | 12.6 |  |  | 3470
37 | (SNP-STP-005) 7 MLD STP Ganaur Sonepat by PHED in 1.1.2012 (MBBR) |  | 30 | 7.0-8.5 | 100 | 40
[11 empty] | 06.01.2026 | 1896 dt. 15.01.2026 |  | 1: 7.26; 2: 8.4; 3: 48.4; 5: 17; 11: 9.84; 25: 79 |  |  |  | Complying | Complying |  | 7.49 | 90 | 368 |  | 230 | [5 empty] | 39.13 | [13 empty] | 6300
[11 empty] | 09.02.2026 | 2291, dt. 17.02.2026 |  | 1: 7.22; 2: 6.4; 3: 31.7; 5: 14; 11: 7; 25: 63 |  |  |  | Complying | Complying |  | 7.56 | 95 | 388.8 |  | 205 | [5 empty] | 40.24 | [13 empty] | 8400
[11 empty] | 06.03.2026 | 2536, 16.03.2026 |  | 1: 7.05; 2: 7.8; 3: 44; 5: 18; 11: 8.12; 25: 79 |  |  |  | Complying | Complying |  | 8.13 | 96 | 384 |  | 245 | [5 empty] | 42.13 | [13 empty] | 9300
[11 empty] | 13.04.2026 | 110, dt. 23.04.2026 |  | 1: 7.97; 2: 8.6; 3: 44.3; 5: 15; 11: 7; 25: 84 |  |  |  | Complying | Complying |  | 7.96 | 125 | 491.9 |  | 280 | [5 empty] | 47.24 | [13 empty] | 6300
[11 empty] | 25.05.2026 | 337, dt. 03.06.2026 |  | 1: 7.2; 2: 8.6; 3: 44; 5: 8; 25: 63 |  |  |  | Complying | Complying |  | 7.37 | 82 | 376 |  | 190 | [19 empty] | 7900
[11 empty] | 05.06.2026 | 421, dt. 18.06.2026 |  | 1: 7.44; 2: 5.2; 3: 32; 5: 340; 11: 8.42; 25: 58 |  |  |  | Complying | Complying |  | 8.02 | 88 | 328 |  | 1150 | [5 empty] | 36.24 | [13 empty] | 8400
[11 empty] | 08.07.2026 | 322 M dt. 17.07.2026 |  | 1: 6.65; 2: 4.4; 3: 24; 5: 6; 6: 370; 9: 48; 11: 7.46; 12: 1.58; 25: 63; 52: BDL*(DL**=4); 55: 690 |  |  |  | Complying | Complying |  | 6.48 | 92 | 360 |  | 255 | 890 |  |  | 195 |  | 31.28 | 6.84 | [12 empty] | 5800 | [26 empty] | 7.4
| July, 2nd phase 2026 | [9 empty] | 22.07.2026 | 376 M dt. 30.07.2026 |  | 7.28 | 9.4 | 60 | BDL*(DL**=4) | 24 | 440 | 129.9 | 150 | 75 | 0.45 | 5.6 | 2.07 | 6.2 |  | 3.66 | ND |  | 132.745 | 23.766 | 35.581 |  |  | 230 | 270 | 58 |  |  | 4.23 |  |  | 0.212 | BDL*(DL**=0.0004) | 0.08 | 0.028 | BDL*(DL**=0.00082) | BDL*(DL**=0.0005) | BDL*(DL**=0.001) | BDL*(DL**=0.001) | BDL*(DL**=0.00041) | BDL*(DL**=0.0002) | 0.006 | 0.003 | BDL*(DL**=0.001) | 0.046 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.079 | BDL*(DL**=0.0006) |  |  |  | 790 |  |  |  | Non-Complying | Non-Complying |  | 7.23 | 98 | 384 | 7.2 | 280 | 450 | 124.9 | 80 | 2.33 | 2.33 | 28.02 | 4.42 | 4.7 |  | 4.34 | 1.6 |  | 102.748 | 36.888 | 67.491 |  |  | 80 | 280 | 6300 |  |  | 2.5 |  |  | 0.255 | 0.062 | 39.94 | 0.6 | 0.095 | 0.07 | 0.343 | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.331 | 0.66 | BDL*(DL**=0.001) | 1.066 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.141 | BDL*(DL**=0.0006) |  |  |  | 810
[11 empty] | 06.08.2026 | 667 M dt. 18.08.2026 |  | 6.85 | 8.4 | 44 |  | 16 | 580 | 142.4 | 245 | 58 | 0.56 | 4.48 | BDL*(DL**=0.5) | 1.3 |  | 0.98 | ND |  | 78.809 | 24.7 | 40.8 |  |  | 285 | 114 | 93 |  |  | 2.4 |  |  | 0.003 | 0.004 | 0.067 | 0.117 | BDL*(DL**=0.0008) | 0.003 | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.009 | 0.256 | BDL*(DL**=0.001) | 0.006 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.176 | BDL*(DL**=0.0006) | BDL*(DL**=4) |  |  | 1040 |  |  |  | Complying | Complying |  | 6.37 | 115 | 440 |  | 310 | 490 | 127.4 | 50 | 123 | 4.06 | 12.4 | 3.18 | 12.4 |  | 2.45 | 3.2 |  | 63.407 | 19.1 | 31.6 |  |  | 150 | 160 | 8400 |  |  | 2.2 |  |  | 0.008 | 0.71 | 177.732 | 2.529 | 0.415 | 0.219 | 1.925 | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | 0.059 | 0.345 | 3.131 | BDL*(DL**=0.001) | 46.407 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 2.123 | BDL*(DL**=0.0006) | 10.8 |  |  | 870
38 | (SNP-STP-006) 3 MLD STP , Gohana , Sonepat by PHED in 1.11.2015 (MBBR) |  | 30 | 7.0-8.5 | 100 | 40
[11 empty] | 06.01.2026 | 1891 dt. 15.01.2026 | 1.11 | 1: 7.31; 2: 60; 3: 256; 5: 110; 11: 15.6; 25: 840 |  |  |  | Non-Complying | Non-Complying |  | 7.64 | 95 | 384 |  | 240 | [5 empty] | 39.16 | [13 empty] | 8400
[11 empty] | 11.02.2026 | 2310, dt. 18.02.2026 |  | 1: 7.24; 2: 70; 3: 293.6; 5: 75; 11: 14.01; 25: 930 |  |  |  | Non-Complying | Non-Complying |  | 7.52 | 105 | 420.6 |  | 275 | [5 empty] | 40.72 | [13 empty] | 7000
[11 empty] | 12.03.2026 | 2601, dt. 25.03.02026 | 101.74 | 1: 7.32; 2: 75; 3: 304; 5: 82; 11: 21.02; 25: 2900 |  |  |  | Non-Complying | Non-Complying |  | 7.54 | 92 | 384 |  | 210 | [5 empty] | 38.44 | [13 empty] | 7900
[11 empty] | 20.04.2026 | 187, dt. 30.04.2026 | 144.9 | 1: 7.52; 2: 52; 3: 196; 5: 75; 11: 17.68; 25: 2100 |  |  |  | Non-Complying | Non-Complying |  | 7.84 | 110 | 440 |  | 290 | [5 empty] | 44.22 | [13 empty] | 11000
[11 empty] | 27.05.2026 | 356, dt. 04.06.2026 |  | 1: 7.36; 2: 46; 3: 180; 5: 82; 11: 15.96; 25: 2900 |  |  |  | Non-Complying | Non-Complying |  | 7.53 | 115 | 464 |  | 325 | [5 empty] | 41.38 | [13 empty] | 9300
[11 empty] | 10.06.2026 | 212, dt. 18.06.2026 |  | 1: 7.29; 2: 33; 3: 132; 5: 37; 11: 18.02; 25: 1700 |  |  |  | Non-Complying | Non-Complying |  | 7.92 | 96 | 384 |  | 275 | [5 empty] | 32.91 | [13 empty] | 7000
[11 empty] | 07.07.2026 | 304 M dt. 15.07.2026 | 138.23 | 1: 7.15; 2: 23; 3: 84; 5: 42; 6: 1310; 11: 15.19; 25: 1100; 52: 4.4 |  |  |  | Non-Complying | Non-Complying | - | 7.33 | 130 | 488 |  | 340 | 1660 |  |  |  |  | 28.02 | [13 empty] | 8400 | [26 empty] | 7.2
| July, 2nd phase 2026 | [9 empty] | 22.07.2026 | 382 M dt. 03.08.2026 |  | 6.08 | 21 | 132 | BDL*(DL**=4) | 38 | 2190 | 639.7 | 420 | 152 | 0.56 | 17.92 | 2.66 | 1.8 |  | 4.29 | ND |  | 607.5 | 117.018 | 91.076 |  |  | 450 | 755 | 930 |  |  | 9.92 |  |  | 0.421 | BDL*(DL**=0.0016) | 0.289 | 0.157 | BDL*(DL**=0.0008) | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | BDL*(DL**=0.0145) | 0.025 | BDL*(DL**=0.001) | 0.138 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.069 | BDL*(DL**=0.0006) |  |  |  | 3990 |  |  |  | Non-Complying | Non-Complying |  | 7.11 | 120 | 480 | 7.2 | 225 | 1530 | 769.6 | 460 | 165 | 1.25 | 25.28 | 12.72 | 12.5 |  | 5.74 | 6.8 |  | 484.898 | 116.297 | 100.23 |  |  | 760 | 755 | 930 |  |  | 7.81 |  |  | 0.432 | BDL*(DL**=0.0016) | 3.011 | 0.166 | 0.014 | 0.024 | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | BDL*(DL**=0.0145) | 0.073 | BDL*(DL**=0.001) | 5.972 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.275 | BDL*(DL**=0.0006) |  |  |  | 2090
[11 empty] | 07.08.2026 | 656 M dt. 14.08.2026 | not installed | 7.11 | 20 | 128 |  | 48 | 2030 | 724.7 | 275 | 157 | 0.78 | 15.49 | 3.16 | 4.6 |  | 1.87 | ND |  | 510.328 | 79.7 | 131.4 |  |  | 425 | 660 | 210 |  |  | 8.66 |  |  | 0.276 | 0.001 | 0.292 | 0.101 | BDL*(DL**=0.0008) | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | BDL*(DL**=0.0145) | 0.001 | BDL*(DL**=0.001) | 0.066 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.057 | BDL*(DL**=0.0006) | 5.2 |  |  | 3690 |  |  |  | Non-Complying | Non-Complying | not installed | 7.54 | 118 | 464 |  | 220 | 1780 | 693.5 | 480 | 172 | 1.49 | 32.4 | 13.24 | 16.2 |  | 5.37 | 4.2 |  | 499.168 | 71.4 | 117.8 |  |  | 510 | 590 | 11000 |  |  | 8.15 |  |  | 0.312 | 0.026 | 2.012 | 0.204 | 0.029 | 0.013 | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | BDL*(DL**=0.0145) | 0.001 | BDL*(DL**=0.001) | 0.066 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.057 | BDL*(DL**=0.0006) | 10.6 |  |  | 3240
39 | (SNP-STP-007) 8.3 MLD STP Gohana, Sonepat by PHED in 2.7.2012 (MBBR) |  | 30 | 7.0-8.0 | 100 | 50 | [78 empty] | 11.05 |  |  | 0.19
[11 empty] | 06.01.2026 | 1892 dt. 15.01.2026 |  | 1: 7.31; 2: 20; 3: 92; 5: 33; 11: 13.81; 25: 790 |  |  |  | Non-Complying | Non-Complying |  | 7.75 | 102 | 416 |  | 205 | [5 empty] | 34.64 | [13 empty] | 8400
[11 empty] | 11.02.2026 | 2311, dt. 18.02.2026 |  | 1: 7.64; 2: 8.8; 3: 47.6; 5: 16; 11: 7.34; 25: 93 |  |  |  | Complying | Complying |  | 7.81 | 92 | 365.05 |  | 240 | [5 empty] | 32.48 | [13 empty] | 4900
[11 empty] | 12.03.2026 | 2603, dt. 25.03.2026 |  | 1: 7.29; 2: 7.4; 3: 40; 5: 17; 11: 8.4; 25: 79 |  |  |  | Complying | Complying |  | 7.94 | 95 | 368 |  | 220 | [5 empty] | 39.56 | [13 empty] | 5800
[11 empty] | 20.04.2026 | 189, dt. 30.04.2026 |  | 1: 7.43; 2: 6.8; 3: 32; 5: 13; 11: 6.64; 25: 58 |  |  |  | Complying | Complying |  | 7.98 | 105 | 408 |  | 260 | [5 empty] | 28.02 | [13 empty] | 7000
[11 empty] | 27.05.2026 | 357, dt. 04.06.2026 |  | 1: 7.42; 2: 8.4; 3: 48; 5: 17; 11: 7.52; 25: 93 |  |  |  | Complying | Complying |  | 7.84 | 118 | 472 |  | 255 | [5 empty] | 34.92 | [13 empty] | 8400
[11 empty] | 10.06.2026 | 214, dt. 18.06.2026 |  | 1: 7.6; 2: 6.4; 3: 28; 5: 9; 11: 6.52; 25: 80 |  |  |  | Complying | Complying |  | 7.46 | 95 | 384 |  | 240 | [5 empty] | 30.84 | [13 empty] | 7900
[11 empty] | 07.07.2026 | 303 M dt. 15.07.2026 |  | 1: 7.42; 2: 8.4; 3: 32; 5: 13; 6: 610; 11: 7.04; 25: 63; 52: BDL*(DL**=4); 55: 1090 |  |  |  | Complying | Complying |  | 6.46 | 115 | 424 |  | 295 | 1080 |  |  |  |  | 26.29 | [13 empty] | 5800 | [26 empty] | 8.2
| July, 2nd phase 2026 | [9 empty] | 22.07.2026 | 383 M dt. 04.08.2026 |  | 6.92 | 5.2 | 24 | BDL*(DL**=4) | 14 | 710 | 232.4 | 290 | 95 | 0.88 | 10.48 | 2.51 | 3.4 |  | 1.5 | ND |  | 194.644 | 46.261 | 57.468 |  |  | 370 | 425 | 79 |  |  | 4.7 |  |  | 0.244 | BDL*(DL**=0.0016) | 0.097 | 0.094 | BDL*(DL**=0.0008) | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | BDL*(DL**=0.0145) | BDL*(DL**=0.015) | BDL*(DL**=0.001) | BDL*(DL**=0.060) |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.064 | BDL*(DL**=0.0006) |  |  |  | 1280 |  |  |  | Complying | Complying |  | 7.01 | 540 | 2176 | 7.2 | 620 | 790 | 224.9 | 730 | 143 | 2.56 | 32.26 | 5.3 | 1.7 |  | 11.2 | 3.2 |  | 180.968 | 55.2 | 86.716 |  |  | 730 | 600 | 4900 |  |  | 3.74 |  |  | 0.278 | BDL*(DL**=0.006) | 8.501 | 0.252 | 0.024 | 0.031 | 0.16 | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | BDL*(DL**=0.0145) | 0.229 | BDL*(DL**=0.001) | 11.948 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.236 | BDL*(DL**=0.0006) |  |  |  | 1450
[11 empty] | 07.08.2026 | 655 M dt. 14.08.2026 |  | 7.19 | 7.8 | 48 | BDL*(DL**=4) | 18 | 820 | 212.4 | 345 | 121 | 0.76 | 7.84 | 2.12 | 2.1 |  | 0.82 | ND |  | 220.125 | 32.8 | 54.1 |  |  | 355 | 272 | 84 |  |  | 5.88 |  |  | 0.108 | 0.001 | 0.053 | 0.031 | BDL*(DL**=0.0008) | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | BDL*(DL**=0.0145) | BDL*(DL**=0.0009) | BDL*(DL**=0.001) | 0.022 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.051 | BDL*(DL**=0.0006) |  |  |  | 1480 |  |  |  | Complying | Complying |  | 7.03 | 280 | 1080 | 9.8 | 540 | 870 | 297.4 | 690 | 155 | 1.99 | 29.28 | 4.48 | 11.8 |  | 5.6 | 2.2 |  | 276.209 | 34.5 | 56.9 |  |  | 690 | 288 | 9300 |  |  | 7.13 |  |  | 0.229 | 0.007 | 6.075 | 0.106 | 0.056 | 0.064 | 0.125 | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.007) | BDL*(DL**=0.0145) | BDL*(DL**=0.0009) | BDL*(DL**=0.001) | 5.098 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.103 | BDL*(DL**=0.0006) |  |  |  | 1590
40 | (SNP-STP-008) 15 MLD STP Sonepat (Aterna) by HSVP in 30.04.2024 | [9 empty] | under commissioning (mail received on 21.04.2026 via RO)
41 | (SNP-STP-009) 3 MLD, STP Murthal Sonepat by ULBD in 31.12.2024 | [9 empty] | 13.04.2026 | 112, dt. 23.04.2026 | 2.14 | 1: 7.36; 2: 13; 3: 68.5; 5: 17; 11: 23.16; 25: 180 |  |  |  | Non-Complying | Non-Complying | 2.24 | 7.45 | 105 | 467.7 |  | 270 | [5 empty] | 40.48 | [13 empty] | 9300
[11 empty] | 25.05.2026 | 336, dt. 03.06.2026 |  | 1: 7.52; 2: 5.8; 3: 36; 5: 7; 25: 58 |  |  |  | Complying | Complying |  | 6.86 | 110 | 456 |  | 275 | [19 empty] | 7000
[11 empty] | 05.06.2026 | 422, dt. 18.06.2026 |  | 1: 7.58; 2: 13; 3: 68; 5: 32; 11: 13.92; 25: 93 |  |  |  | Non-Complying | Non-Complying |  | 7.62 | 105 | 376 |  | 255 | [5 empty] | 26.84 | [13 empty] | 5800
[11 empty] | 08.07.2026 | 321 M dt. 17.07.2026 |  | 1: 6.78; 2: 4.6; 3: 28; 5: 9; 6: 390; 9: 71; 12: 1.96; 17: ND; 25: 63; 52: BDL*(DL**=4); 55: 710 |  |  |  | Complying | Complying |  | 6.46 | 95 | 392 |  | 240 | 820 |  |  | 370 |  |  | 8.2 |  |  |  |  | 0.74 | [7 empty] | 8400 | [26 empty] | 7.6 |  |  | 1490
| July, 2nd phase 2026 | [9 empty] | 22.07.2026 | 385 M dt. 04.08.2026 |  | 7.23 | 15 | 60 | BDL*(DL**=4) | 18 | 690 | 184.9 | 340 | 86 | 0.45 | 8.24 | 2.23 | 2.8 |  | 0.98 | ND |  | 243.413 | 38.947 | 50.691 |  |  | 400 | 340 | 58 |  |  | 6.23 |  |  | 0.188 | BDL*(DL**=0.0016) | 0.109 | 0.089 | BDL*(DL**=0.0008) | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.006 | 0.011 | BDL*(DL**=0.001) | 0.08 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.046 | BDL*(DL**=0.0006) |  |  |  | 1250 |  |  |  | Non-Complying | Non-Complying |  | 6.94 | 150 | 456 | 7.2 | 290 | 790 | 209.9 | 880 | 93 | 2.39 | 27.12 | 2.79 | 1.9 |  | 11.86 | 1.6 |  | 252.45 | 46.528 | 56.462 |  |  | 880 | 560 | 4900 |  |  | 6.02 |  |  | 0.202 | BDL*(DL**=0.0016) | 4.104 | 0.185 | 0.12 | 0.029 | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.017 | 0.143 | BDL*(DL**=0.001) | 5.857 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.14 | BDL*(DL**=0.0006) |  |  |  | 1440
[11 empty] | 10.08.2026 | 666 M dt. 14.08.2026 |  | 7.02 | 6.8 | 40 |  | 17 | 370 | 122.4 | 150 | 59 | 0.37 | 5.6 | 1.12 | 1.8 |  | 1.87 | ND |  | 88.529 | 21.3 | 35.2 |  |  | 170 | 180 | 63 |  |  | 2.06 |  |  | BDL*(DL**=0.0024) | 0.002 | 0.018 | 0.023 | BDL*(DL**=0.0008) | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.009 | 0.012 | BDL*(DL**=0.001) | 0.007 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.042 | BDL*(DL**=0.0006) | BDL*(DL**=4) |  |  | 680 |  |  |  | Complying | Complying |  | 6.87 | 115 | 360 |  | 245 | 1070 | 359.8 | 420 | 126 | 3.19 | 25.24 | 9.18 | 12.4 |  | 5.28 | 3.2 |  | 244.631 | 43.1 | 70.9 |  |  | 570 | 360 | 7900 |  |  | 4 |  |  | BDL*(DL**=0.0024) | 0.002 | 0.018 | 0.023 | BDL*(DL**=0.0008) | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | BDL*(DL**=0.0145) | BDL*(DL**=0.0009) | BDL*(DL**=0.001) | 0.6 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.052 | BDL*(DL**=0.0006) | 8.2 |  |  | 1940
Jhajjar
42 | (JHJ-STP-004) 5.5 MLD STP Kosli Road, Jhajjar by PHED in March dt. 2007 (MBBR) |  | 30 | 7.0 to 8.5 | 100 | 50
[11 empty] | 01.01.2026 | 1856 dt. 08.01.2026 |  | 1: 7.23; 2: 9.2; 3: 44; 5: 18; 11: 8.24; 25: 63 |  |  |  | Complying | Complying |  | 7.79 | 98 | 392 |  | 285 | [5 empty] | 42.17 | [13 empty] | 8400
[11 empty] | 04.02.2026 | 2245 dt. 12.02.2026 |  | 1: 7.18; 2: 8.8; 3: 36; 5: 16; 11: 7; 25: 70 |  |  |  | Complying | Complying |  | 7.06 | 102 | 416 |  | 245 | [5 empty] | 38.14 | [13 empty] | 9300
[11 empty] | 06.03.2026 | 2546 dt. 17.03.2026 |  | 1: 7.33; 2: 7.6; 3: 40; 5: 17; 11: 7.84; 25: 93 |  |  |  | Complying | Complying |  | 7.48 | 105 | 424 |  | 265 | [5 empty] | 42.72 | [13 empty] | 7000
[11 empty] | 07.04.2026 | 61 dt. 15.04.2026 |  | 1: 7.45; 2: 6.8; 3: 32; 5: 19; 11: 7.12; 25: 79 | [7 empty] | 96
[11 empty] | 31.05.2026 | 523-524 dt. 09.06.2026 |  | 1: 6.6; 2: 5; 3: 36; 5: 8; 11: BDL; 25: 63 |  |  |  | Complying | Complying |  | 6.5 | 165 | 1440 |  | 101 | [5 empty] | 23 | [13 empty] | 84000
[11 empty] | 05.06.2026 | 574-575 dt. 11.06.2026 |  | 1: 7.7; 2: 7; 3: 44; 5: 12; 11: -; 25: 53 |  |  |  | Complying | Complying |  | 7.8 | 135 | 492 |  | 157 | [5 empty] | - | [13 empty] | 134000
[11 empty] | 02.07.2026 | 793-794 dt.11.07.2026 |  | 1: 7.6; 2: 8; 3: 28; 5: 10; 11: BDL; 14: BDL; 25: 51; 52: BDL; 55: 1110 |  |  |  | Complying | Complying |  | 7.3 | 110 | 288 |  | 188 | [5 empty] | 17 |  |  | 3 | [10 empty] | 11500 | [26 empty] | 6 |  |  | 1860
[11 empty] | 06.08.2026 | 1399-1400 dt. 13.08.2026 |  | 1: 6.6; 2: 7; 3: 28; 5: 14; 9: BDL; 10: BDL; 11: 3.1; 12: BDL; 13: BDL; 14: 0.2; 15: BDL; 16: BDL; 17: BDL; 19: 35; 20: 50; 24: 130; 25: 65; 28: 0.8; 31: BDL; 33: BDL; 35: BDL; 36: BDL; 42: BDL; 52: BDL; 55: 1540 |  |  |  | Complying | Complying |  | 6.7 | 110 | 372 |  | 215 |  |  |  | 210 | 1.6 | 26.4 | 12.4 | 0.4 | 2.6 | 2.3 | BDL | BDL |  | 50 | 130 |  |  |  | 240 | 78000 |  |  | 6.2 |  |  | BDL |  | BDL |  | BDL | BDL | [5 empty] | BDL | [9 empty] | 6 |  |  | 1671
43 | (JHJ-STP-005) 5 MLD STP Sampla Road , Jhajjar by PHED in 3.11.2014 (MBBR) |  | 30 | 7.0 to 8.5 | 100 | 50
[11 empty] | 01.01.2026 | 1855 dt. 08.01.2026 |  | 1: 7.19; 2: 6.8; 3: 40; 5: 15; 11: 6.63; 25: 84 |  |  |  | Complying | Complying |  | 7.84 | 84 | 320 |  | 220 | [5 empty] | 39.44 | [13 empty] | 7900
[11 empty] | 04.02.2026 | 2244 dt. 12.02.2026 |  | 1: 7.26; 2: 7.4; 3: 44; 5: 18; 11: 7.12; 25: 93 |  |  |  | Complying | Complying |  | 7.12 | 85 | 376 |  | 260 | [5 empty] | 40.12 | [13 empty] | 6300
[11 empty] | 06.03.2026 | 2547 dt. 17.03.2026 |  | 1: 7.29; 2: 8.2; 3: 48; 5: 16; 11: 9.84; 25: 93 |  |  |  | Complying | Complying |  | 7.55 | 95 | 424 |  | 245 | [5 empty] | 38.72 | [13 empty] | 8400
[11 empty] | 07.04.2026 | 62 dt. 15.04.2026 |  | 1: 7.35; 2: 11; 3: 56; 5: 24; 11: 11.6; 25: 130 | [6 empty] | 7.84 | 104 | 432 |  | 260 | [5 empty] | 39.56 | [13 empty] | 9300
[11 empty] | 31.05.2026 | 525-526 dt. 09.06.2026 |  | 1: 6.5; 2: 5; 3: 44; 5: 13; 11: BDL; 25: 91 |  |  |  | Complying | Complying |  | 6.8 | 370 | 2080 |  | 166 | [5 empty] | 21 | [13 empty] | 193000
[11 empty] | 05.06.2026 | 570-571 dt. 11.06.2026 |  | 1: 7.2; 2: 4; 3: 20; 5: 14; 11: -; 25: 45 |  |  |  | Complying | Complying |  | 7.1 | 115 | 396 |  | 252 | [5 empty] | - | [13 empty] | 84000
[11 empty] | 02.07.2026 | 795-796 dt.11.07.2026 |  | 1: 7.5; 2: 8; 3: 36; 5: 17; 11: BDL; 14: BDL; 25: 58; 52: BDL; 55: 1550 |  |  |  | Complying | Complying |  | 7.3 | 115 | 304 |  | 134 | [5 empty] | 18 |  |  | 4 | [10 empty] | 12000 | [26 empty] | 4 |  |  | 2020
[11 empty] | 06.08.2026 | 1397-1398 dt. 13.08.2026 | Detail not provided | 1: 6.7; 2: 6; 3: 28; 5: 15; 9: 68.5; 10: BDL; 11: 6.2; 12: 3.2; 13: 2.3; 14: 0.2; 15: BDL; 16: BDL; 17: BDL; 19: 36; 20: 62; 24: 115; 25: 83; 28: 3.8; 31: BDL; 33: BDL; 35: BDL; 36: BDL; 42: BDL; 52: BDL; 55: 1955 |  |  |  | Complying | Complying | Detail not provided | 6.8 | 110 | 292 |  | 197 |  |  |  | 84.5 | BDL | 46.5 | 25.4 | 14.6 | 2.3 | 1.8 | BDL | BDL |  | 42 | 74 |  |  |  | 145 | 57000 |  |  | 18.6 |  |  | BDL |  | BDL |  | BDL | BDL | [5 empty] | BDL | [9 empty] | 13.5 |  |  | 1892
44 | (JHJ-STP-007) 3.0 MLD STP Beri town, Beri, Jhajjar by PHED dt. 31.03.2022 | [73 empty] | 6.8 | 118 | 472 |  | 185 | [5 empty] | 15.7 | [13 empty] | -
[11 empty] | 01.01.2026 | 1854 dt. 08.01.2026 |  | 1: 7.24; 2: 7.2; 3: 48; 5: 17; 11: 7.12; 25: 79 | [6 empty] | 7.75 | 92 | 368 |  | 225 | [5 empty] | 32.16 | [13 empty] | 9300
[11 empty] | 04.02.2026 | 246 dt. 12.02.2026 |  | 1: 7.21; 2: 9.2; 3: 40; 5: 18; 11: 6.84; 25: 58 |  |  |  | Complying | Complying |  | 7.85 | 82 | 328 |  | 240 | [5 empty] | 28.02 | [13 empty] | 4900
[11 empty] | 06.03.2026 | 2548 dt. 17.03.2026 |  | 1: 7.28; 2: 22; 3: 96; 5: 32; 11: 11.72; 25: 140 |  |  |  | Non-Complying | Non-Complying |  | 7.51 | 110 | 448 |  | 235 | [5 empty] | 39.48 | [13 empty] | 6900
[11 empty] | 07.04.2026 | 59 dt. 15.04.2026 |  | 1: 7.55; 2: 24; 3: 104; 5: 42; 11: 12.96; 25: 240 |  |  |  | Non-Complying | Non-Complying |  | 8.02 | 120 | 488 |  | 245 | [5 empty] | 40.72 | [13 empty] | 7900
[11 empty] | 06.05.2026 | 63-64 dt. 14.05.2026 |  | 1: 7; 2: 8; 3: 48; 5: 18; 11: 3; 25: 92 |  |  |  | Complying | Complying |  | 6.7 | 130 | 440 |  | 176 | [5 empty] | 17 | [13 empty] | 21000
[11 empty] | 10.06.2026 | 633-634 dt. 19.06.2026 |  | 1: 7.7; 2: 7; 3: 36; 5: 12; 11: BDL; 25: 71 |  |  |  | Complying | Complying |  | 7.6 | 165 | 436 |  | 327 | [5 empty] | 25 | [13 empty] | 184000
[11 empty] | 02.07.2026 | 781-782 dt.10.07.2026 |  | 1: 7.8; 2: 9; 3: 44; 5: 11; 11: BDL; 14: BDL; 25: 58; 52: BDL |  |  |  | Complying | Complying |  | 7.7 | 105 | 356 |  | 172 | [5 empty] | 11.8 |  |  | 4.2 | [10 empty] | 12000 | [26 empty] | 5
[11 empty] | 07.08.2026 | 1471-1472 dt. 13.08.2026 | 33.793 | 1: 6.9; 2: 8; 3: 40; 5: 17; 9: 74; 10: BDL; 11: 6.2; 12: 2.4; 13: 1.3; 14: 0.3; 15: BDL; 16: BDL; 17: BDL; 19: 56; 20: 84; 24: 196; 25: 78; 28: 4.2; 31: BDL; 33: BDL; 35: BDL; 36: BDL; 42: BDL; 52: BDL; 55: 1702 |  |  |  | Complying | Complying | 100.07 | 6.9 | 90 | 312 |  | 218 |  |  |  | 168 | 0.2 | 28.2 | 14.5 | 9.6 | 2.4 | 1.9 | 1.2 | BDL |  | 75 | 140 |  |  |  | 232 | 117000 |  |  | 14.2 |  |  | BDL |  | BDL |  | BDL | BDL | [5 empty] | BDL | [9 empty] | 17 |  |  | 1702
Bahadurgarh
45 | (JHJ-STP-001) 18 MLD STP,Linepar, Bahadurgarh by PHED, October, 2012 (UASB+EA) |  | 10 | 5-9.00 | 250 | 100
[11 empty] | 07.01.2026 | 1913 dt. 19.01.2026 |  | 1: 7.64; 2: 68; 3: 306.4; 5: 130; 11: 18.21; 25: 930 |  |  |  | Non-Complying | Non-Complying |  | 7.21 | 102 | 419.3 |  | 195 | [5 empty] | 34.72 | [13 empty] | 8400
[11 empty] | 06.02.2026 | 2279 dt. 14.02.2026 |  | 1: 7.29; 2: 72; 3: 298.3; 5: 125; 11: 20.24; 25: 1100 |  |  |  | Non-Complying | Non-Complying |  | 7.26 | 80 | 330.6 |  | 205 | [5 empty] | 48.26 | [13 empty] | 4100
[11 empty] | 05.03.2026 | 2526 dt. 13.03.2026 |  | 1: 7.28; 2: 85; 3: 328; 5: 140; 11: 21.72; 25: 2100
[11 empty] | 06.04.2026 | 32 dt. 13.04.2026 |  | 1: 7.22; 2: 90; 3: 368; 5: 160; 11: 24.12; 25: 3300
[11 empty] | 14.05.2026 | 173-174 dt. 23.05.2026 |  | 1: 7.8; 2: 90; 3: 236; 5: 134; 11: 18; 25: 116000 |  |  |  | Non-Complying | Non-Complying |  | 7.1 | 110 | 512 |  | 318 | [5 empty] | 36 | [13 empty] | 213000
[11 empty] | 10.06.2026 | 616-617 dt. 19.06.2026 |  | 1: 8.1; 2: 165; 3: 516; 5: 126; 11: 34; 25: 92000 |  |  |  | Non-Complying | Non-Complying |  | 7.8 | 135 | 460 |  | 110 | [5 empty] | 29 | [13 empty] | 87000
[11 empty] | 02.07.2026 | 791-792 dt.11.07.2026 |  | 1: 7.6; 2: 65; 3: 144; 5: 112; 11: 8.4; 14: 2; 25: 6000; 52: 4; 55: 5830 |  |  |  | Non-Complying | Non-Complying |  | 7.7 | 145 | 312 |  | 184 | [5 empty] | 14 |  |  | 5.2 | [10 empty] | 15000 | [26 empty] | 5 |  |  | 5820
[11 empty] | 07.08.2026 | 1481-1482 dt. 13.08.2026 | Not installed | 1: 6.6; 2: 70; 3: 184; 5: 111; 9: 72; 10: BDL; 11: 9.8; 12: 2.1; 13: 7.3; 14: 0.3; 15: BDL; 16: BDL; 17: BDL; 19: 52; 20: 86; 24: 184; 25: 15000; 28: 4.2; 31: BDL; 33: BDL; 35: BDL; 36: BDL; 42: BDL; 52: 7; 55: 787 |  |  |  | Non-Complying | Non-Complying | Not installed | 6.7 | 105 | 292 |  | 150 |  |  |  | 104 | BDL | 45.8 | 28.5 | 16.2 | 2.6 | 2.1 | BDL | BDL |  | 86 | 122 |  |  |  | 240 | 57000 |  |  | 13.6 |  |  | BDL |  | BDL |  | BDL | BDL | [5 empty] | BDL | [9 empty] | 13 |  |  | 784
46 | (JHJ-STP-002) 36 MLD STP Najafgarh Road, Bahadurgarh by PHED in 1.4.2014 (SBR) |  | 10 | 6.5 to 9 | 50 | <20
[11 empty] | 07.01.2026 | 1915 dt. 19.01.2026 |  | 1: 7.73; 2: 8.8; 3: 44.3; 5: 15; 11: 8.24; 25: 81 |  |  |  | Non-Complying | Non-Complying |  | 7.82 | 102 | 411.2 |  | 235 | [5 empty] | 49.13 | [13 empty] | 7800
[11 empty] | 04.02.2026 | 2248 dt. 12.02.2026 |  | 1: 7.13; 2: 6.8; 3: 32; 5: 13; 11: 9.8; 25: 70 |  |  |  | Complying | Complying |  | 7.96 | 90 | 368 |  | 265 | [5 empty] | 42.14 | [13 empty] | 5800
[11 empty] | 06.03.2026 | 2549 dt. 17.03.2026 |  | 1: 7.2; 2: 76; 3: 320; 5: 170; 11: 15.61; 25: 840 |  |  |  | Non-Complying | Non-Complying |  | 8.13 | 95 | 392 |  | 250 | [5 empty] | 32.82 | [13 empty] | 7900
[11 empty] | 07.04.2026 | 60 dt. 15.04.2026 |  | 1: 7.44; 2: 82; 3: 368; 5: 150; 11: 17.84; 25: 990 |  |  |  | Non-Complying | Non-Complying |  | 7.78 | 105 | 440 |  | 305 | [5 empty] | 39.64 | [13 empty] | 9300
[11 empty] | 22.05.2026 | 349-350 dt. 01.06.2026 |  | 1: 7; 2: 60; 3: 160; 5: 40; 11: 18; 25: 1400 |  |  |  | Non-Complying | Non-Complying |  | 7 | 135 | 468 |  | 182 | [5 empty] | 32 | [13 empty] | 132000
[11 empty] | 10.06.2026 | 620-621 dt. 18.06.2026 |  | 1: 7.8; 2: 55; 3: 136; 5: 46; 11: BDL; 25: 1600 |  |  |  | Non-Complying | Non-Complying |  | 8.5 | 115 | 436 |  | 358 | [5 empty] | 23 | [13 empty] | 87000
[11 empty] | 07.07.2026 | 871-872 dt. 20.07.2026 |  | 1: 7.8; 2: 45; 3: 120; 5: 58; 11: 19; 25: 8400; 52: 4; 55: 2260 |  |  |  | Non-Complying | Non-Complying |  | 7.1 | 85 | 328 |  | 136 | [5 empty] | 34 | [13 empty] | 76000 | [29 empty] | 1197
[11 empty] | 07.08.2026 | 1469-1470 dt. 13.08.2026 | Detail not provided | 1: 6.8; 2: 65; 3: 184; 5: 51; 9: 166; 10: BDL; 11: 6.7; 12: 3.6; 13: 2.5; 14: 2.8; 15: 0.7; 16: BDL; 17: BDL; 19: 48; 20: 86; 24: 142; 25: 94000; 28: 7.6; 31: BDL; 33: BDL; 35: BDL; 36: BDL; 42: BDL; 52: BDL; 55: 1084 |  |  |  | Non-Complying | Non-Complying | Detail not provided | 6.7 | 125 | 348 |  | 202 |  |  |  | 234 | BDL | 42 | 21.4 | 15.6 | 3.7 | 2.4 | 0.5 | BDL |  | 74 | 126 |  |  |  | 194 | 112000 |  |  | 21.4 |  |  | BDL |  | BDL |  | BDL | BDL | [5 empty] | BDL | [9 empty] | 4 |  |  | 980
47 | (JHJ-STP-003) 10 MLD STP Beri Road, Jhajjar, Bahadurgarh by HUDA in 2.2.2013 (EPA)
[11 empty] | 07.01.2026 | 1912 dt. 19.01.2026 |  | 1: 7.29; 2: 7.8; 3: 40.4; 5: 14; 11: 7.12; 25: 58 |  |  |  | Complying | Complying |  | 7.24 | 82 | 330.6 |  | 230 | [5 empty] | 39.64 | [13 empty] | 7000
[11 empty] | 04.02.2026 | 2249 dt. 12.02.2026 |  | 1: 7.65; 2: 9.2; 3: 48; 5: 18; 11: 8.4; 25: 63 |  |  |  | Complying | Complying |  | 8.19 | 85 | 320 |  | 210 | [5 empty] | 32.16 | [13 empty] | 9300
[11 empty] | 24.03.2026 | 2656 dt. 01.04.2026 |  | 1: 7.34; 2: 18; 3: 76; 5: 28; 11: 18.56; 25: 7900 |  |  |  | Non-Complying | Non-Complying |  | 7.82 | 120 | 488 |  | 255 | [5 empty] | 48.72 | [13 empty] | 9300
[11 empty] | 07.04.2026 | 57 dt. 15.04.2026 |  | 1: 7.31; 2: 8.2; 3: 40; 5: 18; 11: 9.26; 25: 3300 |  |  |  | Complying | Complying |  | 7.54 | 92 | 368 |  | 225 | [5 empty] | 31.55 | [13 empty] | 7900
[11 empty] | 22.05.2026 | 353-354 dt. 01.06.2026 |  | 1: 7.1; 2: 8; 3: 32; 5: 12; 11: BDL; 25: 75 |  |  |  | Complying | Complying |  | 7.3 | 115 | 382 |  | 98 | [5 empty] | 26 | [13 empty] | 146500
[11 empty] | 09.06.2026 | 618-619 dt. 18.06.2026 |  | 1: 6.9; 2: 6; 3: 40; 5: 5; 11: BDL; 25: 73 |  |  |  | Complying | Complying |  | 7.1 | 75 | 368 |  | 222 | [5 empty] | 26 | [13 empty] | 183000
[11 empty] | 07.07.2026 | 869-870 dt. 20.07.2026 |  | 1: 7.4; 2: 16; 3: 72; 5: 32; 11: 5; 25: 1200; 52: BDL; 55: 3070 |  |  |  | Non-Complying | Non-Complying |  | 7.2 | 120 | 336 |  | 126 | [5 empty] | 24 | [13 empty] | 67000 | [29 empty] | 1197
[11 empty] | 05.08.2026 | 1373-1374 dt. 13.08.2026 | 304.8 | 1: 6.8; 2: 8; 3: 40; 5: 12; 9: 82; 10: BDL; 11: 7.2; 12: 2.4; 13: 4.6; 14: BDL; 15: 0.3; 16: BDL; 17: BDL; 19: 35; 20: 85; 24: 170; 25: 75; 28: 4.6; 31: BDL; 33: BDL; 35: BDL; 36: BDL; 42: BDL; 52: BDL; 55: 2500 |  |  |  | Complying | Complying | 631.9 | 6.7 | 70 | 312 |  | 207 |  |  |  | 172 | BDL | 24.5 | 12.2 | 8.4 | 2.2 | 2.7 | BDL | BDL |  | 40 | 160 |  |  |  | 265 | 82000 |  |  | 21.4 |  |  | BDL |  | BDL |  | BDL | BDL | [5 empty] | BDL | [9 empty] | 4 |  |  | 980
Rohtak
48 | (RTK-STP-001) 19.5 MLD STP, PGIIMS , Rohtak by PHED in 31.3.2016 (SBR) |  | 10 | 6.5 to 8.00 | 50 | 10
[11 empty] | 05.01.2026 | 1865 dt 14.01.2026 | 96.5 | 1: 7.19; 2: 8.2; 3: 48; 5: 17; 11: 6.84; 25: 70 |  |  |  | Complying | Complying | 191.4 | 7.21 | 102 | 416 |  | 240 | [5 empty] | 36.32 | [13 empty] | 5800
[11 empty] | 04.02.2026 | 2261 dt 13.02.2026 |  | 1: 6.97; 2: 6.2; 3: 32.2; 5: 12; 11: 7.68; 25: 84 |  |  |  | Complying | Complying |  | 7.47 | 72 | 304.1 |  | 250 | [5 empty] | 32.28 | [13 empty] | 6000
[11 empty] | 06.03.2026 | 2519 dt 13.03.2026 | 305.6 | 1: 7.12; 2: 6.2; 3: 28; 5: 18; 11: 6.72; 25: 93 |  |  |  | Complying | Complying | 642.6 | 7.24 | 82 | 328 |  | 210 | [5 empty] | 39.26 | [13 empty] | 8400
[11 empty] | 07.04.2026 | 70 dt 17.04.2026 |  | 1: 7.04; 2: 7.6; 3: 32; 5: 15; 11: 7.24; 25: 70 |  |  |  | Complying | Complying | 181.78 | 7.28 | 92 | 368 |  | 225 | [5 empty] | 34.72 | [13 empty] | 6300
[11 empty] | 07.05.2026 | 79-80-A dt 13.05.2026 | 291.31 | 1: 8.2; 2: 9; 3: 42; 5: 17; 11: 7.2; 25: 82 |  |  |  | Complying | Complying | 211.67 | 6.7 | 156 | 468 |  | 356 | [5 empty] | 18.6 | [13 empty] | 11000
[11 empty] | 08.06.2026 | 281-282-A,B dt 16.06.2026 | 440.5 | 1: 7.7; 2: 8; 3: 42; 5: 13; 11: 7; 25: 72 |  |  |  | Complying | Complying | 425.4 | 7.4 | 120 | 472 |  | 306 | [5 empty] | 21.2 | [13 empty] | 120000
[11 empty] | 07.07.2026 | 457-458-A dt. 14.07.2026 |  | 1: 7.5; 2: 8; 3: 40; 5: 14; 25: 56; 52: BDL(DL=4); 55: 1424 | 8 |  |  | Complying | Complying |  | 7.8 | 112 | 448 |  | 272 | [19 empty] | 3.8X104 | [26 empty] | 21 |  |  | 4856
| July, 2026 2nd Phase | [9 empty] | 22.07.2026 | HRL/WW-II/2026/609-610-A dt. 06.08.2026 |  | 1: 7.3; 2: 7.5; 3: 32; 5: 12; 6: 492; 7: 170.6; 8: 210.5; 9: 172.1; 18: 57; 19: 37.7; 20: 42.1; 23: 175; 24: 260; 25: 78; 28: 9; 29: 4.5; 30: 1012; 31: 0.9; 52: BDL(DL=4) |  | BDL |  | Complying | Complying |  | 7.8 | 102 | 308 |  | 212 | 972 | 481.8 | 512.4 | 362.1 | [8 empty] | 265 | 160.4 | 120.2 |  |  | 420 | 960 | 4.8X104 |  |  | 22.4 | 15.6 | 2412 | 1.8 | [20 empty] | 36 |  |  |  |  | 2.1
[11 empty] | 07.08.2026 | 736-737-A dt. 21.08.2026 | Flow meter installed but not working | 1: 7.1; 2: 7.2; 3: 28; 5: 8; 6: 432; 7: 144.8; 8: 85.4; 9: 165.4; 18: 52; 19: 38.9; 20: 136.1; 23: 160; 24: 240; 25: 72; 28: 7.3; 29: 1.4; 30: 976; 31: 6.2; 52: BDL(DL=4) |  | 1.8 | 0.4 | Complying | Complying | Flow meter installed but not working | 7.5 | 96 | 276 |  | 194 | 1148 | 379.4 | 463.4 | 326.5 | [8 empty] | 242 | 64.1 | 112.2 |  |  | 380 | 840 | 4.2X104 |  |  | 31.7 | 13.2 | 2248 | 0.6 | [20 empty] | 28 |  |  |  |  | 2.3 | 5.8
49 | (RTK-STP-002) 40 MLD STP, Sonariyan , Rohtak, PHED, 31.03.2016 |  | 30 | 7.0 to 7.5 | 250 | 100
[11 empty] | 05.01.2026 | 1864 dt 14.01.2026 |  | 1: 7.73; 2: 88; 3: 344; 5: 210; 11: 30.16; 25: 8400 |  |  |  | Non complying | Non complying |  | 8.24 | 120 | 484 |  | 275 | [5 empty] | 39.14 | [13 empty] | 11000
[11 empty] | 04.02.2026 | 2259 dt 12.02.2026 |  | 1: 6.96; 2: 78; 3: 314.4; 5: 225; 11: 28.02; 25: 9300 |  |  |  | Non complying | Non complying |  | 8.16 | 105 | 427.3 |  | 280 | [5 empty] | 40.028 | [13 empty] | 13000
[11 empty] | 05.03.2026 | 2515 dtd 13.03.2026 |  | 1: 7.09; 2: 85; 3: 352; 5: 245; 11: 25.61; 25: 8400 |  |  |  | Non complying | Non complying |  | 8.14 | 102 | 424 |  | 260 | [5 empty] | 44.72 | [13 empty] | 15000
[11 empty] | 07.04.2026 | 67 dt 17.04.2026 |  | 1: 7.28; 2: 72; 3: 328; 5: 205; 11: 31.56; 25: 9300 |  |  |  | Non complying | Non complying |  | 8.25 | 120 | 488 |  | 255 | [5 empty] | 38.54 | [13 empty] | 13000
[11 empty] | 08.05.2026 | 83-84-A,B dt 13.05.2026 |  | 1: 7.4; 2: 64; 3: 160; 5: 114; 25: 3600 |  |  |  | Non complying | Non complying |  | 8.5 | 126 | 436 |  | 312 | [19 empty] | 8600
[11 empty] | 02.06.2026 | 250-51A,B dt 08.06.2026 |  | 1: 7.2; 2: 38; 3: 112; 5: 112; 11: 8.2; 25: 150 |  |  |  | Non complying | Non complying |  | 8.2 | 108 | 456 |  | 292 | [5 empty] | 22.2 | [13 empty] | 4800
[11 empty] | 07.07.2026 | 451-452-A dt. 14.07.2026 |  | 1: 7.9; 2: 42; 3: 152; 5: 122; 25: 2.4X104; 52: BDL(DL=4); 55: 2560 | 9 |  |  | Non complying | Non complying |  | 8.4 | 102 | 392 |  | 248 | [19 empty] | 4.2X104 | [26 empty] | 18 |  |  | 3960
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | HRL/WW-II/2026/593-594-A dt. 04.08.2026 |  | 1: 8; 2: 38; 3: 56; 5: 41; 6: 632; 7: 230.9; 8: 353.2; 9: 231.5; 18: 125; 19: 45; 20: 70.1; 23: 290; 24: 360; 25: 86; 28: 16.5; 29: 6; 30: 1916; 31: 1.5; 52: BDL(DL=4) |  | 0.8 |  | Non complying | Non complying |  | 8.8 | 120 | 360 |  | 272 | 826 | 522 | 683.2 | 321.5 | [8 empty] | 224 | 111.8 | 200.4 |  |  | 560 | 960 | 4.5X104 |  |  | 17.9 | 10.4 | 2114 | 2.8 | [20 empty] | 22 |  |  |  |  | 2.6
[11 empty] | 07.08.2026 | 730-731-A dt. 21.08.2026 | Flow meter not installed | 1: 8.2; 2: 28; 3: 60; 5: 40; 6: 1448; 7: 174.7; 8: 305; 9: 248.7; 18: 148; 19: 154; 20: 128.3; 23: 250; 24: 960; 25: 80; 28: 12.4; 29: 9.2; 30: 3642; 31: 5.6; 52: 9 |  | 1.5 | 0.8 | Non complying | Non complying | 257.1 | 8.6 | 128 | 336 |  | 256 | 1878 | 419.3 | 512.4 | 529.8 | [8 empty] | 342.8 | 160.3 | 248.5 |  |  | 420 | 1280 | 5.2X104 |  |  | 24 | 9.2 | 3642 | 5.6 | [20 empty] | 28 |  |  |  |  | 2.8 | 5.6
50 | (RTK-STP-003) 3.5 MLD STP Kalanour , Rohtak by PHED in 1.10.2010 |  | 30 | 7.0 to 7.5 | 250 | 100
[11 empty] | 05.01.2026 | 1867 dt 14.01.2026 | 96.5 | 1: 7.34; 2: 7.8; 3: 36; 5: 15; 11: 9.12; 25: 93 |  |  |  | Complying | Complying | 191.4 | 7.11 | 90 | 368 |  | 230 | [5 empty] | 41.13 | [13 empty] | 6300
[11 empty] | 04.02.2026 | 2260 dt 12.02.2026 |  | 1: 7.1; 2: 8.4; 3: 40.3; 5: 13; 11: 8.54; 25: 73 |  |  |  | Complying | Complying |  | 7.67 | 85 | 346.7 |  | 205 | [5 empty] | 37.09 | [13 empty] | 5800
[11 empty] | 05.03.2026 | 2522 dt 13.03.2026 | 110.1 | 1: 7.15; 2: 7.4; 3: 40; 5: 15; 11: 7.29; 25: 89 |  |  |  | Complying | Complying |  | 7.29 | 84 | 352 |  | 245 | [5 empty] | 39.28 | [13 empty] | 7500
[11 empty] | 07.04.2026 | 69 dt 17.04.2026 | 129.7 | 1: 7.13; 2: 6.2; 3: 36; 5: 12; 11: 6.24; 25: 58 |  |  |  | Complying | Complying |  | 7.21 | 78 | 328 |  | 195 | [5 empty] | 30.33 | [13 empty] | 8400
[11 empty] | 08.05.2026 | 95-96-A,B dt 13.05.2026 | 145.5 | 1: 7.2; 2: 7.1; 3: 32; 5: 17; 11: 5.8; 25: 64 |  |  |  | Complying | Complying |  | 8.9 | 86 | 356 |  | 232 | [5 empty] | 28.2 | [13 empty] | 18000
[11 empty] | 08.06.2026 | 289-290 A,B dt 16.06.2026 | 179.7 | 1: 7.4; 2: 7.8; 3: 28; 5: 15; 11: 6.4; 25: 68 |  |  |  | Complying | Complying |  | 8.7 | 96 | 408 |  | 240 | [5 empty] | 36.4 | [13 empty] | 24000
[11 empty] | 06.07.2026 | 443-444-A dt. 14.07.2026 |  | 1: 7.2; 2: 7.2; 3: 24; 5: 12; 25: 62; 52: BDL(DL=4); 55: 1080 | 7 |  |  | Complying | Complying |  | 8.4 | 90 | 352 |  | 232 | [19 empty] | 1.8X104 | [26 empty] | 22 |  |  | 3642
| July, 2026 2nd Phase | [9 empty] | 22.07.2026 | HRL/WW-II/2026/613-614-A dt. 06.08.2026 |  | 1: 7.4; 2: 7.2; 3: 42; 5: 8; 6: 392; 7: 173.1; 8: 347.7; 9: 145.3; 18: 42; 19: 36.5; 20: 48.1; 23: 285; 24: 270; 25: 80; 28: 6.5; 29: 14.8; 30: 2428; 31: 1.6; 52: BDL(DL=4) |  | 0.9 |  | Complying | Complying |  | 8.1 | 112 | 332 |  | 198 | 970 | 351.3 | 707.6 | 284.3 | [8 empty] | 165 | 160.4 | 200.4 |  |  | 580 | 1160 | 2.1X104 |  |  | 12.3 | 14.8 | 2428 | 1.6 | [20 empty] | 32 |  |  |  |  | 1.8
[11 empty] | 06.08.2026 | 708-709-A dt. 21.08.2026 | 128.2 | 1: 7.3; 2: 7.3; 3: 24; 5: 6.8; 6: 438; 7: 94.6; 8: 219.6; 9: 106.8; 18: 48; 19: 24.3; 20: 48.1; 23: 180; 24: 220; 25: 64; 28: 8; 29: 3.2; 30: 1228; 31: 0.8; 52: BDL(DL=4) |  | 0.8 | 0.7 | Complying | Complying | Flow meter not working | 7.9 | 90 | 308 |  | 136 | 1356 | 349.4 | 683.2 | 218.5 | [8 empty] | 220 | 68 | 224.4 |  |  | 560 | 840 | 2.2X104 |  |  | 18.2 | 5.6 | 2620 | 2.1 | [20 empty] | 24 |  |  |  |  | 2.1 | 6.1
51 | (RTK-STP-004) 5 MLD STP, Meham , Bharan Road , Rohtak by PHED January dt. 2013 |  | 30 | 7 to 8 | 100 | 50
[11 empty] | 05.01.2026 | 1869 dt. 14.01.2026 | 47.4 | 1: 7.16; 2: 6.4; 3: 32; 5: 12; 11: 5.6; 25: 49 |  |  |  | Complying | Complying |  | 7.45 | 98 | 392 |  | 270 | [5 empty] | 32.33 | [13 empty] | 3900
[11 empty] | 04.02.2026 | 2253 dt 12.02.2026 | 114.5 | 1: 7.82; 2: 8.2; 3: 48.3; 5: 19; 11: 6.8; 25: 84 |  |  |  | Complying | Complying |  | 7.89 | 102 | 419.3 |  | 250 | [5 empty] | 30.64 | [13 empty] | 4100
[11 empty] | 05.03.2026 | 2516 dt 13.03.2026 | 82.2 | 1: 7.05; 2: 8.4; 3: 44; 5: 17; 11: 8.72; 25: 93 |  |  |  | Complying | Complying |  | 8.13 | 110 | 448 |  | 255 | [5 empty] | 34.26 | [13 empty] | 7000
[11 empty] | 08.04.2026 | 72 dt 17.04.2026 | 52 | 1: 7.16; 2: 8.4; 3: 48; 5: 17; 11: 9.96; 25: 70 |  |  |  | Complying | Complying |  | 8.29 | 115 | 464 |  | 270 | [5 empty] | 39.12 | [13 empty] | 9300
[11 empty] | 08.05.2026 | 91-92-A,B dt 13.05.2026 | 73.7 | 1: 8.2; 2: 8.5; 3: 32; 5: 7; 11: 9.2; 25: 56 |  |  |  | Complying | Complying |  | 8.8 | 106 | 456 |  | 256 | [5 empty] | 34.2 | [13 empty] | 28000
[11 empty] | 08.06.2026 | 285-286 A,B dt 16.06.2026 | 118 | 1: 7.9; 2: 8.2; 3: 28; 5: 9; 11: 9; 25: 68 |  |  |  | Complying | Complying |  | 9.2 | 96 | 298 |  | 212 | [5 empty] | 32.8 | [13 empty] | 24000
[11 empty] | 06.07.2026 | 439-440-A dt. 14.07.2026 |  | 1: 7.6; 2: 7.8; 3: 32; 5: 8; 25: 72; 52: BDL(DL=4); 55: 1780 | 10 |  |  | Complying | Complying |  | 9.1 | 90 | 280 |  | 196 | [19 empty] | 2.1X104 | [26 empty] | 24 |  |  | 4250
| July, 2026 2nd Phase | [9 empty] | 22.07.2026 | HRL/WW-II/2026/607-608-A dt. 06.08.2026 |  | 1: 7.6; 2: 7.5; 3: 28; 5: 12; 6: 432; 7: 135.5; 8: 195.8; 9: 123.4; 18: 62; 19: 27.9; 20: 28.1; 23: 160; 24: 185; 25: 56; 28: 11.7; 29: 4.1; 30: 948; 31: 0.8; 52: BDL(DL=4) |  | 0.7 |  | Complying | Complying |  | 8.4 | 96 | 416 |  | 224 | 820 | 491.9 | 536.8 | 342.1 | [8 empty] | 192 | 165.2 | 96.2 |  |  | 440 | 920 | 2.4X104 |  |  | 16.8 | 17.6 | 2142 | 2 | [20 empty] | 42 |  |  |  |  | 2.5
[11 empty] | 21.08.2026 | 706-707-A dt. 21.08.2026 | Flow meter not working | 1: 7.5; 2: 7.8; 3: 36; 5: 9; 6: 456; 7: 90; 8: 146.2; 9: 132.1; 18: 36; 19: 55.9; 20: 84.2; 23: 240; 24: 440; 25: 72; 28: 4.3; 29: 2.8; 30: 956; 31: 0.6; 52: BDL(DL=4) |  | 0.8 | 0.6 | Complying | Complying | Flow meter not working | 8.2 | 118 | 348 |  | 148 | 1148 | 359.4 | 561.2 | 245.2 | [8 empty] | 140 | 102.1 | 200.4 |  |  | 460 | 920 | 1.8X104 |  |  | 11.4 | 7.6 | 2552 | 1.4 | [20 empty] | 28 |  |  |  |  | 1.6 | 5.7
52 | (RTK-STP-005) 10 MLD STP Singhpura, Rohtak by ULBD in February, 2012 |  | 30 | 7.0 to 7.5 | 250 | 100
[11 empty] | 07.01.2026 | 1917 dt. 19.01.2026 | 3001 | 1: 7.09; 2: 6.4; 3: 28.2; 5: 13; 11: 7; 25: 49 |  |  |  | Complying | Complying |  | 7.33 | 84 | 346.7 |  | 245 | [5 empty] | 34.48 | [13 empty] | 6300
[11 empty] | 04.02.2026 | 2255 dt 12.02.2026 | 228.25 | 1: 7.53; 2: 8.4; 3: 40.3; 5: 15; 11: 5.6; 25: 93 |  |  |  | Complying | Complying |  | 7.77 | 78 | 314.3 |  | 265 | [5 empty] | 33.84 | [13 empty] | 5800
[11 empty] | 05.03.2026 | 2523 dt 13.03.2026 | 238.2 | 1: 7.35; 2: 6.8; 3: 32; 5: 13; 11: 7; 25: 58 |  |  |  | Complying | Complying |  | 7.92 | 88 | 376 |  | 235 | [5 empty] | 40.26 | [13 empty] | 7100
[11 empty] | 08.04.2026 | 78 dt 17.04.2026 | 98.207 | 1: 7.49; 2: 7.4; 3: 36; 5: 17; 11: 8.32; 25: 79 |  |  |  | Complying | Complying |  | 8.03 | 120 | 448 |  | 290 | [5 empty] | 33.94 | [13 empty] | 8400
[11 empty] | 08.05.2026 | 97-98-A,B dt 13.05.2026 | 238.54 | 1: 7.6; 2: 8.2; 3: 48; 5: 14; 11: 9.1; 25: 86 |  |  |  | Complying | Complying |  | 8.6 | 126 | 486 |  | 324 | [5 empty] | 32.2 | [13 empty] | 28000
[11 empty] | 08.06.2026 | 283-284A,B dt 16.06.2026 | 210 | 1: 7.8; 2: 7.2; 3: 24; 5: 12; 11: 8.2; 25: 72 |  |  |  | Complying | Complying |  | 8.2 | 102 | 724 |  | 228 | [5 empty] | 30.4 | [13 empty] | 32000
[11 empty] | 07.07.2026 | 461-462-A dt. 14.07.2026 |  | 1: 7.9; 2: 8.2; 3: 40; 5: 14; 25: 56; 52: BDL(DL=4); 55: 1020 | 8 |  |  | Complying | Complying |  | 8.3 | 102 | 352 |  | 264 | [19 empty] | 1.8X104 | [26 empty] | 14 |  |  | 2874
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | HRL/WW-II/2026/585-586-A dt. 04.08.2026 | 218 | 1: 7.6; 2: 7.8; 3: 38; 5: 16; 6: 256; 7: 100.4; 8: 268.4; 9: 170; 18: 72; 19: 30.4; 20: 24.1; 23: 220; 24: 185; 25: 90; 28: 13.8; 29: 5.7; 30: 876; 31: BDL; 52: BDL(DL=4) |  | 0.7 |  | Complying | Complying |  | 9.2 | 122 | 336 |  | 212 | 256 | 100.4 | 268.4 | 170 | [8 empty] | 72 | 30.4 | 24.1 |  |  | 220 | 185 | 3.2X104 |  |  | 15.8 | 7 | 2428 | 1.3 | [20 empty] | 26 |  |  |  |  | 2.4
[11 empty] | 07.08.2026 | 732-733-A dt. 21.08.2026 | 222 | 1: 7.2; 2: 8.2; 3: 32; 5: 14; 6: 346; 7: 239.6; 8: 0.4; 9: 175.9; 18: 56.8; 19: 24.3; 20: 36.1; 23: 190; 24: 190; 25: 72; 28: 10.5; 29: 4; 30: 924; 31: 0.9; 52: BDL(DL=4) |  | 0.8 | 0.5 | Complying | Complying | Flow meter not installed | 8.9 | 114 | 308 |  | 196 | 1148 | 519.1 | 927.2 | 282.4 | [8 empty] | 190.4 | 116.6 | 184.4 |  |  | 380 | 940 | 3.8X104 |  |  | 13.5 | 15.6 | 2248 | 2.8 | [20 empty] | 28 |  |  |  |  | 0.8 | 0.5
53 | (RTK-STP-006) 14 MLD STP, Singhpura , Rohtak by PHED in 31.3.2015 |  | 10 | 6.5 to 8.00 | 50 | 10
[11 empty] | 07.01.2026 | 1916 dt. 19.01.2026 | 3718 | 1: 7.42; 2: 7.4; 3: 36.2; 5: 18; 11: 7.12; 25: 79 |  |  |  | Complying | Complying | 3633 | 7.55 | 90 | 354.8 |  | 275 | [5 empty] | 30.82 | [13 empty] | 8400
[11 empty] | 04.02.2026 | 2254 dt 12.02.2026 | 3673 | 1: 7.7; 2: 7.2; 3: 32.2; 5: 17; 11: 8.4; 25: 79 |  |  |  | Complying | Complying |  | 7.87 | 95 | 370.9 |  | 245 | [5 empty] | 42.26 | [13 empty] | 7000
[11 empty] | 05.03.2026 | 2524 dt 13.03.2026 | 3673 | 1: 7.23; 2: 8.2; 3: 48; 5: 19; 11: 7.92; 25: 93 |  |  |  | Complying | Complying |  | 8.12 | 98 | 392 |  | 295 | [5 empty] | 47.54 | [13 empty] | 9600
[11 empty] | 08.04.2026 | 75 dt 17.04.2026 | 180.1 | 1: 7.02; 2: 7.2; 3: 32; 5: 13; 11: 6.78; 25: 70 |  |  |  | Complying | Complying |  | 7.81 | 110 | 448 |  | 240 | [5 empty] | 41.82 | [13 empty] | 7900
[11 empty] | 08.05.2026 | 85-86-A,B dt 13.05.2026 | 36.33 | 1: 7.4; 2: 7.4; 3: 48; 5: 12; 11: 7.1; 25: 56 |  |  |  | Complying | Complying |  | 8.2 | 120 | 482 |  | 360 | [5 empty] | 34.8 | [13 empty] | 72000
[11 empty] | 08.06.2026 | 279-280A,B dt 16.06.2026 | 240 | 1: 7.8; 2: 8.6; 3: 44; 5: 15; 11: 9; 25: 80 |  |  |  | Complying | Complying |  | 8.5 | 110 | 408 |  | 296 | [5 empty] | 28.2 | [13 empty] | 24000
[11 empty] | 07.07.2026 | 463-464-A dt. 14.07.2026 |  | 1: 7.2; 2: 8; 3: 32; 5: 11; 25: 64; 52: BDL(DL=4); 55: 564 | 12 |  |  | Complying | Complying |  | 8.4 | 96 | 368 |  | 196 | [19 empty] | 2.1X104 | [26 empty] | 19 |  |  | 3648
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | HRL/WW-II/2026/581-582-A dt. 04.08.2026 | Not working | 1: 7.3; 2: 7.4; 3: 32; 5: 14; 6: 392; 7: 148.1; 8: 73.2; 9: 136.2; 18: 36; 19: 24.3; 20: 30.6; 23: 60; 24: 175; 25: 72; 28: 6.9; 29: 1.7; 30: 1050; 31: BDL; 52: BDL(DL=4) |  | 0.9 |  | Complying | Complying |  | 8.1 | 102 | 216 |  | 132 | 928 | 421.6 | 353.8 | 321.7 | [8 empty] | 142 | 97.2 | 184.3 |  |  | 290 | 860 | 4.8X104 |  |  | 11.9 | 4.6 | 2460 | 1.6 | [20 empty] | 28 |  |  |  |  | 5.6
[11 empty] | 07.08.2026 | 734-735-A dt. 21.08.2026 | Flow meter installed but not working | 1: 7.5; 2: 6.5; 3: 28; 5: 10; 6: 223; 7: 94.8; 8: 85.4; 9: 128.4; 18: 42; 19: 24.3; 20: 48.1; 23: 70; 24: 160; 25: 86; 28: 7; 29: 1; 30: 886; 31: 1.1; 52: BDL(DL=4) |  | 0.8 | 0.3 | Complying | Complying |  | 8.2 | 88 | 192 |  | 122 | 846 | 319.4 | 305 | 286.2 | [8 empty] | 156 | 145.8 | 96.2 |  |  | 250 | 420 | 4.5X104 |  |  | 14.2 | 12.2 | 2248 | 2.4 | [20 empty] | 24 |  |  |  |  | 4.9 | 5.4
54 | (RTK-STP-007) 20 MLD STP Rohtak, Kanheli Road, HUDA on 30.8.2024 |  | 10 | 6.5 to 8.00 | 50 | 10
[11 empty] | 05.01.2026 | 1863 dt. 14.01.2026 |  | 1: 7.21; 2: 7.2; 3: 44; 5: 16; 11: 8; 25: 79 |  |  |  | Complying | Complying | 2001 | 7.35 | 84 | 336 |  | 210 | [5 empty] | 34.12 | [13 empty] | 7000
[11 empty] | 04.02.2026 | 2262 dt 12.02.2026 |  | 1: 6.4; 2: 9.2; 3: 40.3; 5: 14; 11: 7.16; 25: 63 |  |  |  | Complying | Complying |  | 7.48 | 90 | 362.8 |  | 320 | [5 empty] | 30.84 | [13 empty] | 4900
[11 empty] | 05.03.2026 | 2524 dt 13.03.2026 | 3673 | 1: 7.23; 2: 8.2; 3: 48; 5: 19; 11: 7.92; 25: 93 |  |  |  | Complying | Complying |  | 8.12 | 98 | 392 |  | 295 | [5 empty] | 47.54 | [13 empty] | 9600
[11 empty] | 07.04.2026 | 68 dt 17.04.2026 |  | 1: 7.62; 2: 4.8; 3: 24; 5: 16; 11: 7; 25: 63 |  |  |  | Complying | Complying | 87.146 | 6.23 | 104 | 424 |  | 220 | [5 empty] | 28.12 | [13 empty] | 7900
[11 empty] | 08.05.2026 | 81-82-A,B dt 13.05.2026 |  | 1: 7.6; 2: 4.9; 3: 41; 5: 14; 11: 7.2; 25: 62 |  |  |  | Complying | Complying | 97.58 | 6.8 | 116 | 486 |  | 282 | [5 empty] | 24.2 | [13 empty] | 120000
[11 empty] | 02.06.2026 | 248-249A,B dt 08.06.2026 |  | 1: 7.8; 2: 4.8; 3: 44; 5: 11; 11: 7.4; 25: 56 |  |  |  | Complying | Complying | 78.81 | 7.1 | 108 | 464 |  | 264 | [5 empty] | 24.6 | [13 empty] | 1800
[11 empty] | 06.07.2026 | 447-448-A dt. 14.07.2026 |  | 1: 7.4; 2: 6.8; 3: 32; 5: 9; 25: 56; 52: BDL(DL=4); 55: 1156 | 9 |  |  | Complying | Complying |  | 7.8 | 96 | 280 |  | 186 | [19 empty] | 5.6X104 | [26 empty] | 18 |  |  | 2842
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | HRL/WW-II/2026/585-586-A dt. 04.08.2026 | Flow meter not installed | 1: 7.3; 2: 7.6; 3: 42; 5: 14; 6: 348; 7: 95.4; 8: 189.9; 9: 151.4; 18: 42; 19: 30.4; 20: 28.1; 23: 155; 24: 195; 25: 86; 28: 7.8; 29: 4.2; 30: 948; 31: BDL; 52: BDL(DL=4) |  | 0.6 |  | Complying | Complying |  | 8.9 | 108 | 308 |  | 148 | 872 | 431.7 | 427 | 321.4 | [8 empty] | 177 | 111.8 | 144.3 |  |  | 350 | 820 | 2.4X104 |  |  | 15.6 | 9 | 2546 | 1.6 | [20 empty] | 28 |  |  |  |  | 2.5
[11 empty] | 06.08.2026 | 712-713-A dt. 21.08.2026 | Not installed but as per scada-537 | 1: 8; 2: 9.7; 3: 38; 5: 12; 6: 290; 7: 144.8; 8: 207.4; 9: 168.2; 18: 48; 19: 24.3; 20: 28.1; 23: 170; 24: 170; 25: 72; 28: 9.4; 29: 4; 30: 746; 31: 0.6; 52: BDL(DL=4) |  | 0.8 | 8.9 | Complying | Complying | 697 | 8.6 | 142 | 104 |  | 248 | 824 | 419.3 | 829.6 | 282.4 | [8 empty] | 156 | 102.1 | 144.3 |  |  | 340 | 780 | 2.8X104 |  |  | 14.1 | 14.8 | 2490 | 3.2 | [20 empty] | 26 |  |  |  |  | 2.4 | 8.9
55 | (RTK-STP-008) 4 MLD STP Sampla Town Rohtak by PHED in 2011 |  | 30 | 6.5 to 8.00 | 250 | 100
[11 empty] | 05.01.2026 | 1868 dt. 14.01.2026 | 81 | 1: 7.26; 2: 8.6; 3: 40; 5: 14; 11: 7.84; 25: 41 |  |  |  | Complying | Complying | 88.6 | 7.76 | 88 | 344 |  | 190 | [5 empty] | 44.12 | [13 empty] | 7900
[11 empty] | 04.02.2026 | 2256 dt 12.02.2026 | 82 | 1: 7.52; 2: 7.6; 3: 32.2; 5: 18; 11: 7.08; 25: 58 |  |  |  | Complying | Complying |  | 8.06 | 98 | 395.1 |  | 220 | [5 empty] | 41.06 | [13 empty] | 6300
[11 empty] | 05.03.2026 | 2512 dt 13.03.2026 | 38.1 | 1: 6.84; 2: 17; 3: 104; 5: 25; 11: 12.6; 25: 630 |  |  |  | Non complying | Non complying |  | 7.96 | 86 | 352 |  | 240 | [5 empty] | 33.42 | [13 empty] | 7000
[11 empty] | 08.04.2026 | 74 dt 17.04.2026 | 77 | 1: 7.465; 2: 6.4; 3: 36; 5: 17; 11: 9.84; 25: 84 |  |  |  | Complying | Complying | 88.6 | 8.24 | 94 | 376 |  | 285 | [5 empty] | 30.82 | [13 empty] | 9400
[11 empty] | 08.05.2026 | 93-94-A,B dt 13.05.2026 | 73.7 | 1: 8.6; 2: 8.7; 3: 34; 5: 6; 11: 8.4; 25: 68 |  |  |  | Complying | Complying |  | 8.9 | 126 | 448 |  | 272 | [5 empty] | 36.4 | [13 empty] | 36000
[11 empty] | 08.06.2026 | 287-288A,B dt 16.06.2026 |  | 1: 7.8; 2: 8.2; 3: 36; 5: 8; 11: 8.2; 25: 56 |  |  |  | Complying | Complying |  | 8.7 | 118 | 432 |  | 256 | [5 empty] | 32.4 | [13 empty] | 42000
[11 empty] | 06.07.2026 | 445-446-A dt. 14.07.2026 |  | 1: 7.6; 2: 7.8; 3: 32; 5: 14; 25: 46; 52: BDL(DL=4); 55: 1612 | 7 |  |  | Complying | Complying |  | 8.2 | 112 | 416 |  | 224 | [19 empty] | 3.6X104 | [26 empty] | 18 |  |  | 4283
| July, 2026 2nd Phase | [9 empty] | 22.07.2026 | HRL/WW-II/2026/615-616-A dt. 06.08.2026 |  | 1: 7.2; 2: 7.1; 3: 28; 5: 7; 6: 320; 7: 155.6; 8: 323.3; 9: 156.3; 18: 42; 19: 29.2; 20: 42.1; 23: 265; 24: 225; 25: 56; 28: 7; 29: 5.6; 30: 1048; 31: 0.7; 52: BDL(DL=4) |  | 0.7 |  | Complying | Complying |  | 7.8 | 96 | 316 |  | 142 | 948 | 341.3 | 323.3 | 156.3 | [8 empty] | 42 | 29.2 | 42.1 |  |  | 265 | 225 | 2.4X104 |  |  | 12.6 | 10 | 2412 | 2.6 | [20 empty] | 32 |  |  |  |  | 3.2
[11 empty] | 06.08.2026 | 710-711-A dt. 21.08.2026 | Flow meter not working | 1: 7.1; 2: 7.2; 3: 32; 5: 9; 6: 420; 7: 124.8; 8: 280; 9: 152.4; 18: 68; 19: 26.7; 20: 32.1; 23: 230; 24: 190; 25: 80; 28: 12.5; 29: 5.2; 30: 1224; 31: 0.8; 52: BDL(DL=4) |  | 0.9 | 0.6 | Complying | Complying | Flow meter not working | 7.9 | 102 | 292 |  | 132 | 912 | 289.3 | 597.3 | 256.4 | [8 empty] | 120 | 77.8 | 176.3 |  |  | 490 | 760 | 5.6X104 |  |  | 10.6 | 7.4 | 2212 | 2.1 | [20 empty] | 24 |  |  |  |  | 2.8 | 4.2
56 | (RTK-STP-009) 12 MLD STP, Garhi Bohar, Rohtak by ULBD in 31.03.2022
[11 empty] | 07.01.2026 | 1918 dt. 19.01.2026 |  | 1: 7.24; 2: 9; 3: 40.3; 5: 18; 11: 7.28; 25: 49 |  |  |  | Complying | Complying | 7000 | 7.72 | 96 | 395.1 |  | 265 | [5 empty] | 34.16 | [13 empty] | 6300
[11 empty] | 04.02.2026 | 2251 dt 12.02.2026 |  | 1: 7.02; 2: 8.4; 3: 44.3; 5: 15; 11: 6.82; 25: 53 |  |  |  | Complying | Complying | 314 | 7.36 | 90 | 362.8 |  | 230 | [5 empty] | 28.14 | [13 empty] | 7000
[11 empty] | 05.03.2026 | 2518 dt 13.03.2026 |  | 1: 7.17; 2: 16; 3: 80; 5: 32; 11: 12.61; 25: 330 |  |  |  | Complying | Complying | 144 | 7.96 | 102 | 416 |  | 275 | [5 empty] | 32.13 | [13 empty] | 8900
[11 empty] | 08.04.2026 | 73 dt 17.04.2026 |  | 1: 6.998; 2: 7.8; 3: 40; 5: 15; 11: 9.12; 25: 84 |  |  |  | Complying | Complying | 217.54 | 7.24 | 88 | 352 |  | 260 | [5 empty] | 39.56 | [13 empty] | 7900
[11 empty] | 07.05.2026 | 77-78-A,B dt 13.05.2026 | 2402 | 1: 7.9; 2: 8.8; 3: 42; 5: 14; 11: 7.8; 25: 72 |  |  |  | Complying | Complying | 2284 | 7.2 | 96 | 342 |  | 242 | [5 empty] | 22.4 | [13 empty] | 9600
[11 empty] | 02.06.2026 | 254-255-A,B dt 08.06.2026 |  | 1: 7.3; 2: 5.2; 3: 28; 5: 8; 11: 6.2; 25: 64 |  |  |  | Complying | Complying | 1878 | 7.2 | 104 | 360 |  | 216 | [5 empty] | 30.2 | [13 empty] | 72000
[11 empty] | 06.07.2026 | 441-442-A dt. 14.07.2026 |  | 1: 7.5; 2: 6.2; 3: 36; 5: 9; 25: 56; 52: BDL(DL=4); 55: 1116 | 8 |  |  | Complying | Complying |  | 7.8 | 108 | 328 |  | 192 | [19 empty] | 5.6X104 | [26 empty] | 14 |  |  | 3852
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | HRL/WW-II/2026/583-584-A dt. 04.08.2026 | Flow meter not installed | 1: 7.5; 2: 8.2; 3: 48; 5: 12; 6: 242; 7: 82.8; 8: 213.5; 9: 128.4; 18: 48; 19: 37.7; 20: 28.6; 23: 175; 24: 225; 25: 72; 28: 8.4; 29: 5.2; 30: 846; 31: 0.5; 52: BDL(DL=4) |  | 0.8 |  | Complying | Complying |  | 8.6 | 112 | 248 |  | 242 | 948 | 461.8 | 390.4 | 281.2 | [8 empty] | 156 | 111.8 | 152.3 |  |  | 320 | 840 | 4.2X104 |  |  | 13.6 | 8 | 2848 | 1.5 | [20 empty] | 32 |  |  |  |  | 3.1
[11 empty] | 06.08.2026 | 704-705-A dt. 21.08.2026 | Flow meter not installed | 1: 7.4; 2: 7.8; 3: 44; 5: 9; 6: 428; 7: 59.9; 8: 146.4; 9: 112.2; 18: 42; 19: 55.9; 20: 84.2; 23: 120; 24: 440; 25: 56; 28: 5; 29: 2.8; 30: 1048; 31: 0.4; 52: BDL(DL=4) |  | 0.7 |  | Complying | Complying | 2224 | 8.4 | 110 | 218 |  | 220 | 1428 | 319.4 | 341.6 | 265.2 | [8 empty] | 148 | 92.3 | 96.2 |  |  | 280 | 620 | 3.5X104 |  |  | 15.2 | 8.4 | 2642 | 1.3 | [20 empty] | 34 |  |  |  |  | 2.8 | 6.3
57 | (RTK-STP-010) 10 MLD STP, Rohtak by HSVP in 31.03.2023
[11 empty] | 07.01.2026 | 1918 dt. 19.01.2026 |  | 1: 7.24; 2: 9; 3: 40.3; 5: 18; 11: 7.28; 25: 49 |  |  |  | Complying | Complying | 7000 | 7.72 | 96 | 395.1 |  | 265 | [5 empty] | 34.16 | [13 empty] | 6300
[11 empty] | 04.02.2026 | 2251 dt 12.02.2026 |  | 1: 7.02; 2: 8.4; 3: 44.3; 5: 15; 11: 6.82; 25: 53 |  |  |  | Complying | Complying | 314 | 7.36 | 90 | 362.8 |  | 230 | [5 empty] | 28.14 | [13 empty] | 7000
[11 empty] | 05.03.2026 | 2518 dt 13.03.2026 |  | 1: 7.17; 2: 16; 3: 80; 5: 32; 11: 12.61; 25: 330 |  |  |  | Complying | Complying | 144 | 7.96 | 102 | 416 |  | 275 | [5 empty] | 32.13 | [13 empty] | 8900
[11 empty] | 08.04.2026 | 73 dt 17.04.2026 |  | 1: 6.998; 2: 7.8; 3: 40; 5: 15; 11: 9.12; 25: 84 |  |  |  | Complying | Complying | 217.54 | 7.24 | 88 | 352 |  | 260 | [5 empty] | 39.56 | [13 empty] | 7900
[11 empty] | 07.05.2026 | 77-78-A,B dt 13.05.2026 | 2402 | 1: 7.9; 2: 8.8; 3: 42; 5: 14; 11: 7.8; 25: 72 |  |  |  | Complying | Complying | 2284 | 7.2 | 96 | 342 |  | 242 | [5 empty] | 22.4 | [13 empty] | 9600
[11 empty] | 02.06.2026 | 254-255-A,B dt 08.06.2026 |  | 1: 7.3; 2: 5.2; 3: 28; 5: 8; 11: 6.2; 25: 64 |  |  |  | Complying | Complying | 1878 | 7.2 | 104 | 360 |  | 216 | [5 empty] | 30.2 | [13 empty] | 72000
[11 empty] | .7.11.2025 | 1552 dt 17.11.2025 |  | 1: 7.29; 2: 6.2; 3: 28.2; 5: 12; 11: 7.14; 25: 41 |  |  |  | Complying | Complying |  | 8.15 | 102 | 411.2 |  | 205 | [5 empty] | 28.02 | [13 empty] | 8400
[11 empty] | 08.12.2025 | 1729 dt 16.12.2025 |  | 1: 7.36; 2: 5.4; 3: 32; 5: 11; 11: 6.68; 25: 49 |  |  |  | Complying | Complying |  | 8.44 | 110 | 448 |  | 270 | [5 empty] | 31.84 | [13 empty] | 6300
[11 empty] | 05.01.2026 | 1866 dt. 14.01.2026 |  | 1: 7.12; 2: 5.8; 3: 28; 5: 13; 11: 4.84; 25: 63 |  |  |  | Complying | Complying |  | 4.49 | 78 | 320 |  | 290 | [5 empty] | 28.02 | [13 empty] | 4900
[11 empty] | 04.02.2026 | 2258 dt 12.02.2026 |  | 1: 6.9; 2: 7.4; 3: 36.2; 5: 16; 11: 7.76; 25: 70 |  |  |  | Complying | Complying |  | 7.78 | 80 | 322.2 |  | 275 | [5 empty] | 36.92 | [13 empty] | 8400
[11 empty] | 05.03.2026 | 2517 dt 13.03.2026 |  | 1: 7.46; 2: 7.6; 3: 32; 5: 14; 11: 7.72; 25: 63 |  |  |  | Complying | Complying |  | 8.29 | 72 | 304 |  | 245 | [5 empty] | 40.84 | [13 empty] | 5800
[11 empty] | 07.04.2026 | 66 dt 17.04.2026 |  | 1: 6.99; 2: 4.6; 3: 28; 5: 11; 11: 7.25; 25: 58 |  |  |  | Complying | Complying |  | 7.24 | 82 | 344 |  | 250 | [5 empty] | 36.72 | [13 empty] | 7000
[11 empty] | 08.05.2026 | 87-88-A,B dt 13.05.2026 |  | 1: 7.6; 2: 7.9; 3: 38; 5: 15; 11: 7.6; 25: 86 |  |  |  | Complying | Complying |  | 8.8 | 96 | 382 |  | 298 | [5 empty] | 32.42 | [13 empty] | 7200
[11 empty] | 02.06.2026 | 256-257 A,B dt 08.06.2026 |  | 1: 7.4; 2: 8.2; 3: 40; 5: 16; 25: 90 |  |  |  | Complying | Complying |  | 8.2 | 112 | 408 |  | 312 | [5 empty] | 24.8 | [13 empty] | 8000
[11 empty] | 06.07.2026 | 449-450-A dt. 14.07.2026 |  | 1: 7.2; 2: 7.2; 3: 36; 5: 11; 25: 86; 52: BDL(DL=4); 55: 952 | 6 |  |  | Complying | Complying |  | 8.3 | 106 | 288 |  | 264 | [19 empty] | 5.6X104 | [26 empty] | 22 |  |  | 4266
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | HRL/WW-II/2026/591-592-A dt. 04.08.2026 |  | 1: 7.5; 2: 8.6; 3: 42; 5: 14; 6: 324; 7: 140.5; 8: 256.2; 9: 153.6; 18: 62; 19: 29.2; 20: 36.1; 23: 210; 24: 210; 25: 36; 28: 10.9; 29: 4.8; 30: 876; 31: 0.8; 52: BDL(DL=4) |  | 0.7 |  | Complying | Complying |  | 8.4 | 112 | 296 |  | 148 | 1324 | 461.8 | 427 | 365.2 | [8 empty] | 194 | 116.6 | 168.3 |  |  | 350 | 900 | 5.6X104 |  |  | 10.9 | 4.8 | 876 | 0.8 | [20 empty] | 28 |  |  |  |  | 2.1
[11 empty] | 06.08.2026 | 704-705-A dt. 21.08.2026 | 172.9 | 1: 7.3; 2: 7.8; 3: 40; 5: 12; 6: 720; 7: 157.7; 8: 268.4; 9: 120.8; 18: 48; 19: 31.6; 20: 44.1; 23: 220; 24: 240; 25: 42; 28: 7.8; 29: 4.8; 30: 720; 31: 0.7; 52: BDL(DL=4) |  | 0.8 | 0.6 | Complying | Complying | Flow meter not installed | 8.4 | 108 | 280 |  | 162 | 1280 | 449.2 | 780.8 | 368.2 | [8 empty] | 156 | 97.2 | 152.3 |  |  | 320 | 780 | 6.4X104 |  |  | 14 | 13.2 | 2620 | 1.3 | [20 empty] | 24 |  |  |  |  | 2.2 | 7.2
58 | (RTK-STP-011) 15 MLD STP, Peer Bodhi, Rohtak by ULBD in 31.12.2023
[11 empty] | 07.01.2026 | 1919 dt. 19.01.2026 |  | 1: 7.24; 2: 7.5; 3: 32.2; 5: 14; 11: 6.64; 25: 70 |  |  |  | Complying | Complying | 5000 | 7.36 | 98 | 403.2 |  | 265 | [5 empty] | 42.18 | [13 empty] | 7900
[11 empty] | 04.02.2026 | 2250 dt 12.02.2026 |  | 1: 7.28; 2: 6.8; 3: 32.2; 5: 15; 11: 7.36; 25: 79 |  |  |  | Complying | Complying | 725 | 7.75 | 95 | 395.1 |  | 245 | [5 empty] | 38.16 | [13 empty] | 5800
[11 empty] | 05.03.2026 | 2521 dt 13.03.2026 |  | 1: 7.16; 2: 6.4; 3: 32; 5: 16; 11: 8.28; 25: 84 |  |  |  | Complying | Complying | 204.253 | 7.35 | 90 | 368 |  | 240 | [5 empty] | 42.13 | [13 empty] | 7100
[11 empty] | 08.04.2026 | 77 dt 17.04.2026 |  | 1: 7.75; 2: 7.4; 3: 28; 5: 14; 11: 6.62; 25: 63 |  |  |  | Complying | Complying | 221.885 | 7.12 | 76 | 320 |  | 205 | [5 empty] | 31.55 | [13 empty] | 5800
[11 empty] | 08.05.2026 | 89-90-A,B dt 13.05.2026 |  | 1: 7.7; 2: 6.8; 3: 42; 5: 11; 11: 5.6; 25: 80 |  |  |  | Complying | Complying | 247.401 | 8.7 | 110 | 426 |  | 312 | [5 empty] | 28.24 | [13 empty] | 11000
[11 empty] | 02.06.2026 | 252-253 A,B dt 08.06.2026 |  | 1: 7.8; 2: 9.2; 3: 44; 5: 14; 11: 7; 25: 86 |  |  |  | Complying | Complying | 5026 | 8.5 | 124 | 464 |  | 228 | [5 empty] | 32.4 | [13 empty] | 80000
[11 empty] | 07.07.2026 | 459-460-A dt. 14.07.2026 |  | 1: 7.6; 2: 8.9; 3: 36; 5: 12; 25: 62; 52: BDL(DL=4); 55: 1556 | 8 |  |  | Complying | Complying |  | 8.2 | 108 | 432 |  | 212 | [19 empty] | 1.2X104 | [26 empty] | 28 |  |  | 4657 | 24
| July, 2026 2nd Phase | [9 empty] | 22.07.2026 | HRL/WW-II/2026/611-612-A dt. 06.08.2026 |  | 1: 7.2; 2: 7.7; 3: 36; 5: 9; 6: 342; 7: 168.1; 8: 341.6; 9: 182.4; 18: 92; 19: 38.9; 20: 42.1; 23: 280; 24: 265; 25: 72; 28: 14.5; 29: 6.7; 30: 912; 31: 0.6; 52: BDL(DL=4) |  | 0.8 |  | Complying | Complying |  | 8.2 | 140 | 288 |  | 196 | 978 | 381.4 | 512.4 | 342.8 | [8 empty] | 174 | 131.2 | 184.4 |  |  | 420 | 1000 | 3.6X104 |  |  | 13.9 | 10 | 2512 | 1.7 | [20 empty] | 28 |  |  |  |  | 2.3
[11 empty] | 07.08.2026 | 728-729-A dt. 21.08.2026 | Flow meter not installed | 1: 7.1; 2: 7.6; 3: 36; 5: 8; 6: 378; 7: 179.7; 8: 329.4; 9: 224.6; 18: 42; 19: 92.3; 20: 136.3; 23: 270; 24: 720; 25: 64; 28: 3.9; 29: 6.2; 30: 920; 31: 0.7; 52: BDL(DL=4) |  | 0.8 | 0.2 | Complying | Complying | 257.1 | 7.9 | 96 | 184 |  | 182 | 1246 | 618.9 | 427 | 282.4 | [8 empty] | 248.6 | 131.2 | 184.4 |  |  | 350 | 1000 | 4.2X104 |  |  | 19.8 | 8.6 | 2510 | 4.8 | [20 empty] | 28 |  |  |  |  | 2.5 | 4.6
Gurgaon North
59 | (GRN-STP-001) 68 MLD STP Dhanwapur, Gurgaon (North) by GMDA in January, 2004 | GMDA | <5 | 6.0 - 8.5 | <50 | Nil |  | 10 | 1 | <100
[11 empty] | 16.01.2026 | 2068 dt. 01.02.2026 |  | 1: 7.24; 2: 22; 3: 80; 5: 55; 11: 7; 25: 68; 52: BDL |  |  |  | Non complying | Non complying |  | 6.72 | 98 | 408 |  | 210 | [5 empty] | 30.86 | [13 empty] | 5800 | [26 empty] | 7.6
[11 empty] | 27.02.2026 | 2497 dt. 11.03.2026 | - | 1: 7.11; 2: 9.2; 3: 48; 5: 18; 11: 7.12; 25: 93; 52: BDL |  |  |  | Complying | Complying | 2767 | 6.76 | 102 | 408 |  | 305 | [5 empty] | 49.56 | [13 empty] | 8400 | [26 empty] | 7.4
[11 empty] | 25.03.2026 | 2664 dt. 01.04.2026 | - | 1: 6.99; 2: 9.2; 3: 48; 5: 19; 11: 9.84; 25: 93; 52: BDL |  |  |  | Complying | Complying | 2706 | 6.78 | 98 | 416 |  | 295 | [5 empty] | 48.34 | [13 empty] | 7900 | [26 empty] | 7.6
[11 empty] | 28.04.2026 | 35-36 dt. 07.05.2026 |  | 1: 6.6; 2: 7; 3: 36; 5: 14; 11: 3; 25: 76 |  |  |  | Complying | Complying |  | 6.6 | 100 | 408 |  | 186 | [5 empty] | 32 | [13 empty] | 44000
[11 empty] | 25.05.2026 | 407-408 dt. 01.06.2026 |  | 1: 6.8; 2: 8; 3: 44; 5: 12; 11: 4; 25: 82 |  |  |  | Complying | Complying |  | 6.6 | 115 | 436 |  | 280 | [5 empty] | 29 | [13 empty] | 56000
[11 empty] | 10.06.2026 | 650-651 dt.18.06.2026 |  | 1: 6.9; 2: 20; 3: 108; 5: 106; 11: 14; 25: 4200; 52: 8 |  |  |  | Non complying | Non complying |  | 6.8 | 95 | 328 |  | 224 | [5 empty] | 32 | [13 empty] | 76000 | [26 empty] | 15 | [7 empty] | 10.06.2026 | 656 dt. 18.06.2026 | 7.1 | 1720 |  |  |  |  | 318.4 | 22.2 |  | 3.4 |  |  | 2.6
60 | (GRN-STP-002) 100 MLD STP Dhanwapur, Gurgoan by GMDA in 1.12.2014 | 25% | <5 | 7-8.5 | <50 | <10
| Jan., 2026 | [132 empty] | 16.01.2026 | 2071 dt. 01.02.2026 | 7.45 | 280 | 0.46 | 11.62 |  | 98.2 | 155 | 21.69 | 630 | 90.3 |  | 1.55
[11 empty] | 27.02.2026 | 2495 dt. 11.03.2026 (Secondary Treatment) |  | 1: 7.27; 2: 32; 3: 136; 5: 55; 11: 15.66; 25: 930; 52: 4.2 |  |  |  | Non complying | Non complying | 4484.7 | 6.39 | 125 | 504 |  | 260 | [5 empty] | 48.48 | [13 empty] | 13000 | [26 empty] | 10.6
[11 empty] | 27.02.2026 | 2495 dt. 11.03.2026 (TertiaryTreatment) |  | 1: 7.62; 2: 15; 3: 68; 5: 29; 11: 11.2; 25: 330; 52: BDL |  |  |  | Non complying | Non complying | 4484.7 | 6.39 | 125 | 504 |  | 260 | [5 empty] | 48.48 | [13 empty] | 13000 | [26 empty] | 10.6
[11 empty] | 25.03.2026 | 2665 dt. 01.04.2026 (Secondary Treatment) | - | 1: 7.18; 2: 30; 3: 120; 5: 40; 11: 12.69; 25: 840; 52: 5.2 |  |  |  | Non complying | Non complying | 4988 | 6.41 | 120 | 488 |  | 235 | [5 empty] | 46.24 | [13 empty] | 15000 | [26 empty] | 12.4
[11 empty] | 25.03.2026 | 2665 dt. 01.04.2026 (TertiaryTreatment) | - | 1: 7.34; 2: 13; 3: 60; 5: 27; 11: 12.6; 25: 290; 52: BDL |  |  |  | Non complying | Non complying | 4988 | 6.41 | 120 | 488 |  | 235 | [5 empty] | 46.24 | [13 empty] | 15000 | [26 empty] | 12.4
[11 empty] | 28.04.2026 | 37-38-39 dt. 07.05.2026 (Secondary Treatment) |  | 1: 6.8; 2: 55; 3: 200; 5: 65; 11: 27; 25: 2700 |  |  |  | Non complying | Non complying |  | 6.8 | 130 | 520 |  | 173 | [5 empty] | 42 | [13 empty] | 38000
[11 empty] | 28.04.2026 | 37-38-39 dt. 07.05.2026 (TertiaryTreatment) |  | 1: 6.7; 2: 25; 3: 160; 5: 36; 11: 15; 25: 1500 |  |  |  | Non complying | Non complying |  | 6.8 | 130 | 520 |  | 173 | [5 empty] | 42 | [13 empty] | 38000
[11 empty] | 25.05.2026 | 409-410-411 dt. 01.06.2026 (Secondary Treatment) |  | 1: 7; 2: 48; 3: 180; 5: 60; 11: 21; 25: 2500 |  |  |  | Non complying | Non complying |  | 6.9 | 115 | 480 |  | 242 | [5 empty] | 36 | [13 empty] | 76000
[11 empty] | 25.05.2026 | 409-410-411 dt. 01.06.2026 (TertiaryTreatment) |  | 1: 6.8; 2: 22; 3: 136; 5: 40; 11: 17; 25: 1300 |  |  |  | Non complying | Non complying |  | 6.9 | 115 | 480 |  | 242 | [5 empty] | 36 | [13 empty] | 76000
[11 empty] | 10.06.2026 | 659-660-661 dt. 18.06.2026 (Secondary Treatment) |  | 1: 7.1; 2: 18; 3: 80; 5: 54; 11: BDL; 25: 1500 |  |  |  | Non complying | Non complying |  | 6.7 | 105 | 348 |  | 212 | [5 empty] | 15 | [13 empty] | 96000
[11 empty] | 10.06.2026 | 659-660-661 dt. 18.06.2026 (TertiaryTreatment) |  | 1: 7.3; 2: 15; 3: 68; 5: 32; 11: BDL; 25: 1200 |  |  |  | Non complying | Non complying |  | 6.7 | 105 | 348 |  | 212 | [5 empty] | 15 | [13 empty] | 96000 | [34 empty] | 10.06.2026 | 655 dt. 18.06.2026 | 7.3 | 1610 |  |  |  |  | 386.8 | 25.2 |  | 3 |  |  | 2.6
61 | (GRN-STP-003) 50 MLD STP Dhanwapur, Gurgaon (North) by ULB/ MCG in 1.10.2018 | GMDA | <5 | 7.0 - 8.0 | <100 | <5 |  | <6 | <0.5 | <100
[11 empty] | 16.01.2026 | 2066 dt. 01.02.2026 | - | 1: 7.24; 2: 5.4; 3: 28; 5: 12; 11: 7; 25: 84; 52: BDL |  |  |  | Complying | Complying | 63 | 7.28 | 85 | 344 |  | 245 | [5 empty] | 36.18 | [13 empty] | 9300 | [26 empty] | 7.6
[11 empty] | 27.02.2026 | 2496 dt. 11.03.2026 | - | 1: 6.71; 2: 4.6; 3: 24; 5: 11; 11: 6.68; 25: 81; 52: BDL |  |  |  | Complying | Complying | 1801 | 7.84 | 120 | 488 |  | 245 | [5 empty] | 33.92 | [13 empty] | 7900 | [26 empty] | 10.2
[11 empty] | 25.03.2026 | 2663 dt. 01.04.2026 | - | 1: 6.32; 2: 8.8; 3: 40; 5: 13; 11: 7.94; 25: 93; 52: BDL |  |  |  | Complying | Complying | 1920 | 7.96 | 1920 | 464 |  | 255 | [5 empty] | 36.72 | [13 empty] | 8400 | [26 empty] | 12.2
[11 empty] | 28.04.2026 | 31-32 dt. 07.05.2026 |  | 1: 7; 2: 8; 3: 40; 5: 10; 11: 2; 25: 82 |  |  |  | Complying | Complying |  | 6.9 | 105 | 420 |  | 225 | [5 empty] | 34 | [13 empty] | 46000
[11 empty] | 25.05.2026 | 405-406 dt. 01.06.2026 |  | 1: 7.1; 2: 7; 3: 40; 5: 16; 11: 1.8; 25: 64 |  |  |  | Complying | Complying |  | 6.9 | 90 | 324 |  | 246 | [5 empty] | 27 | [13 empty] | 92000 | [34 empty] | 10.06.2026 | 657 dt. 18.06.2026 | 7.1 | 1510 |  |  |  |  | 418.2 | 25.6 |  | 2 |  |  | 1.2 | 1.9
[11 empty] | 10.06.2026 | 662-663 dt.18.06.2026 |  | 1: 7; 2: 18; 3: 84; 5: 52; 11: 5; 25: 2400; 52: BDL |  |  |  | Non complying | Non complying |  | 6.8 | 105 | 352 |  | 210 | [5 empty] | 27 | [13 empty] | 94000 | [26 empty] | 18
62 | (GRN-STP-005) 1 MLD STP, Sarai Alawardi, Gurugram North by ULB in 28.02.2021 | [10 empty] | Not operational
63 | (GRN-STP-007) 1 MLD STP, Baliawas, Gurugram North by ULB in 28.02.2021 | [10 empty] | Not operational
64 | (GRN-STP-010) 1 MLD STP, Bandwari (shifted from Sihi/ Khedki Daula), Gurugram North by ULB in 31.10.2021 | [10 empty] | Not operational
65 | (GRN-STP-011) 20 MLD STP, Jhazgarh, Gurugram by GMDA in 31.13.2023
| Jan.,2026 | [10 empty] | No Flow
| Feb.,2026 | [10 empty] | No Flow
| Mar., 2026 | [10 empty] | No Flow
[11 empty] | 28.04.2026 | 33-34 dt. 07.05.2026 |  | 1: 6.8; 2: 7; 3: 44; 5: 16; 11: 4; 25: 86 |  |  |  | Complying | Complying |  | 6.8 | 105 | 312 |  | 160 | [5 empty] | 36 | [13 empty] | 37000
[11 empty] | 25.05.2026 | 411-412 dt. 01.06.2026 |  | 1: 7; 2: 7; 3: 44; 5: 14; 11: 3; 25: 88 |  |  |  | Complying | Complying |  | 6.9 | 100 | 332 |  | 242 | [5 empty] | 27 | [13 empty] | 92000 | [34 empty] | 10.06.2026 | 658 dt. 18.06.2026 | 6.9 | 1680 |  |  |  |  | 376.2 | 19.4 |  | 1.2 |  |  | 1 | 1.6
[11 empty] | 10.06.2026 | 653-654 dt.18.06.2026 |  | 1: 7; 2: 16; 3: 92; 5: 114; 11: 8; 25: 4800; 52: 5 |  |  |  | Non complying | Non complying |  | 6.9 | 100 | 348 |  | 186 | [5 empty] | 27 | [13 empty] | 72000 | [26 empty] | 14
NUH
66 | (NUH-STP-001) 4.5 MLD STP Punhana, Mewat by PHED in 31.12.2015 |  | 20 | 7.00-8.00 | 100 | 40
[11 empty] | 01.01.2026 | 1944 dt. 22.01.2026 |  | 1: 7.28; 2: 8.4; 3: 48.3; 5: 17; 11: 7.12; 25: 63 |  |  |  | Complying | Complying |  | 7.12 | 92 | 395.1 |  | 195 | [5 empty] | 31.84 | [13 empty] | 4900
[11 empty] | 16.02.2026 | 2351 dt. 24.02.2026 |  | 1: 7.09; 2: 5.6; 3: 32; 5: 11; 11: 7.81; 25: 74 |  |  |  | Complying | Complying |  | 7.33 | 80 | 328 |  | 210 | [5 empty] | 46.44 | [13 empty] | 9600
[11 empty] | 11.03.2026 | 2586 dt. 20.03.2026 |  | 1: 7.22; 2: 8.8; 3: 48; 5: 16; 11: 0.44; 25: 93 |  |  |  | Complying | Complying |  | 7.95 | 105 | 424 |  | 275 | [5 empty] | 39.12 | [13 empty] | 5800
[11 empty] | 24.04.2026 | 186 dt. 30.04.2026 |  | 1: 7.67; 2: 7.6; 3: 40; 5: 15; 11: 7.38; 25: 84 |  |  |  | Complying | Complying |  | 7.24 | 98 | 392 |  | 255 | [5 empty] | 35.12 | [13 empty] | 9300
[11 empty] | 21.05.2026 | 301 dt. 29.05.2026 |  | 1: 8.03; 2: 8.6; 3: 44; 5: 11; 11: -; 25: 79 |  |  |  | Complying | Complying |  | 7.21 | 110 | 424 |  | 305 | [5 empty] | - | [13 empty] | 8400
[11 empty] | 02.06.2026 | 398 dt. 10.06.2026 |  | 1: 7.8; 2: 8.4; 3: 36; 5: 17; 11: 5.6; 25: 63 |  |  |  | Complying | Complying |  | 7.94 | 105 | 392 |  | 320 | [5 empty] | 28.02 | [13 empty] | 9300
[11 empty] | 05.07.2026 | 287 M dt. 14.07.2026 |  | 1: 7.57; 2: 8.8; 3: 44; 5: 15; 25: 84; 52: BDL |  |  |  | Complying | Complying |  | 7.12 | 125 | 456 |  | 240 | [19 empty] | 7000
| July, 2nd Phase, 2026 | [9 empty] | 22.07.2026 | 387 M dt. 04.08.2026 |  | 7.87 | 7.8 | 32 |  | 15 | 3360 | 1429.4 | 270 | 198 | 0.88 | 7.81 | BDL*(DL**=0.5) | 2.9 |  | 1.92 | ND |  | 1250.867 | 0.098 | 237.434 |  |  | 510 | 2155 | 79 |  |  | 12.24 |  |  | 0.639 | BDL*(DL**=0.0016) | 0.052 | 0.098 | BDL*(DL**=0.0008) | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.064 | 0.004 | BDL*(DL**=0.001) | 0.077 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.06 | BDL*(DL**=0.0006) | BDL*(DL***=4) |  |  | 6110 |  |  |  | Complying | Complying |  | 7.38 | 120 | 336 |  | 265 | 1790 | 1129.5 | 340 | 252 | 2.59 | 23.96 | 2.8 | 12.8 |  | 9.54 | 2.6 |  | 688.406 | 259.293 | 388.304 |  |  | 460 | 1050 | 6300 |  |  | 6.63 |  |  | BDL*(DL**=0.0024) | 0.78 | 406.215 | 4.934 | 2.2 | 0.587 | 2.524 | BDL*(DL**=0.001) | 0.031 | 0.016 | 0.212 | 6.271 | BDL*(DL**=0.001) | 255.823 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 1.877 | BDL*(DL**=0.0006) | 7.4 |  |  | 3260
67 | (NUH-STP-002) 3.6 MLD Nuh, Mewat by PHED in 25.11.2016 |  | 20 | 7.00-8.00 | 100 | 40
[11 empty] | 07.01.2026 | 1923, 19.01.2026 |  | 1: 7.41; 2: 7.6; 3: 44.3; 5: 14; 11: 8.4; 25: 58 |  |  |  | Complying | Complying |  | 7.75 | 84 | 338.6 |  | 215 | [5 empty] | 42.24 | [13 empty] | 7000
[11 empty] | 11.02.2026 | 2302 dt. 18.02.2026 |  | 1: 7.68; 2: 8.2; 3: 47.6; 5: 19; 11: 6.48; 25: 58 |  |  |  | Complying | Complying |  | 7.19 | 95 | 388.8 |  | 23 | [5 empty] | 40.48 | [13 empty] | 9300
[11 empty] | 11.03.2026 | 2588 dt. 20.03.2026 |  | 1: 7.38; 2: 7.2; 3: 44; 5: 15; 11: 8.4; 25: 84 |  |  |  | Complying | Complying |  | 8.19 | 92 | 392 |  | 265 | [5 empty] | 39.76 | [13 empty] | 7900
[11 empty] | 10.04.2026 | 106 dt. 23.04.2026 |  | 1: 6.71; 2: 8.2; 3: 32.2; 5: 17; 11: 9.28; 25: 79 |  |  |  | Complying | Complying |  | 7.13 | 104 | 322.5 |  | 245 | [5 empty] | 42.14 | [13 empty] | 9300
[11 empty] | 21.05.2026 | 302 dt. 29.05.2026 |  | 1: 7.91; 2: 6.8; 3: 32; 5: 15; 11: 7.52; 25: 63 |  |  |  | Complying | Complying |  | 7.95 | 120 | 488 |  | 255 | [5 empty] | 49.36 | [13 empty] | 7000
[11 empty] | 02.06.2026 | 399 dt. 10.06.2026 |  | 1: 7.56; 2: 5.4; 3: 28; 5: 12; 11: 5.6; 25: 70 |  |  |  | Complying | Complying |  | 8.2 | 108 | 456 |  | 315 | [5 empty] | 42.13 | [13 empty] | 8400
[11 empty] | 03.07.2026 | 282 M dt. 10.07.2026 |  | 1: 7.43; 2: 6.8; 3: 36; 5: 11; 25: 84; 52: BDL |  |  |  | Complying | Complying |  | 7.02 | 90 | 336 |  | 325 | [19 empty] | 7000 | [26 empty] | 8.4
| July, 2nd Phase, 2026 | [9 empty] | 22.07.2026 | 389 M dt. 04.08.2026 |  | 7.8 | 6.8 | 28 |  | 13 | 390 | 59.9 | 95 | 25 | 0.74 | 4.64 | BDL*(DL**=0.5) | 2.1 |  | 0.62 | ND |  | 485.048 | 0.019 | 89.167 |  |  | 105 | 255 | 70 |  |  | 9.14 |  |  | 0.531 | BDL*(DL**=0.0016) | 0.059 | 0.019 | BDL*(DL**=0.0008) | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.027 | BDL*(DL**=0.0009) | BDL*(DL**=0.001) | 0.123 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.028 | BDL*(DL**=0.0006) | BDL*(DL***=4) |  |  | 740 |  |  |  | Complying | Complying |  | 7.35 | 88 | 2790 |  | 205 | 1530 | 754.6 | 150 | 167 | 2.55 | 21.72 | 2.71 | 14.8 |  | 4.58 | 5.6 |  | 427.348 | 0.43 | 75.023 |  |  | 150 | 670 | 3100 |  |  | 8.99 |  |  | 0.594 | BDL*(DL**=0.0016) | 11.296 | 0.43 | 0.039 | 0.077 | 0.185 | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.031 | 0.162 | BDL*(DL**=0.001) | 16.877 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.178 | BDL*(DL**=0.0006) | 9.2 |  |  | 2790
68 | (NUH-STP-003) 4.5 MLD STP Tauru, Mewat by PHED in 30.6.2017 |  | 20 | 7.00-8.00 | 100 | 40
[11 empty] | 08.01.2026 | 1942, 22.01.2026 |  | 1: 7.28; 2: 7.5; 3: 36.02; 5: 18; 11: 5.6; 25: 70 |  |  |  | Complying | Complying |  | 7.38 | 92 | 387.07 |  | 205 | [5 empty] | 30.82 | [13 empty] | 6300
[11 empty] | 13.02.2026 | 2330, 20.02.2026 |  | 1: 7.12; 2: 9.2; 3: 36.2; 5: 15; 11: 8.4; 25: 58 |  |  |  | Complying | Complying |  | 7.23 | 110 | 451.5 |  | 225 | [5 empty] | 42.18 | [13 empty] | 7800
[11 empty] | 11.03.2026 | 2585, 20.03.2026 |  | 1: 7.24; 2: 8.2; 3: 32; 5: 17; 11: 7; 25: 63 |  |  |  | Complying | Complying |  | 7.94 | 95 | 408 |  | 210 | [5 empty] | 46.54 | [13 empty] | 5800
[11 empty] | 09.04.2026 | 101, 22.04.2026 |  | 1: 6.86; 2: 7.4; 3: 36; 5: 16; 11: 6.68; 25: 58 |  |  |  | Complying | Complying |  | 8.02 | 150 | 456 |  | 310 | [5 empty] | 40.24 | [13 empty] | 8400
[11 empty] | 16.05.2026 | 281, 22.05.2026 |  | 1: 7.14; 2: 7.6; 3: 32; 5: 18; 11: 8.36; 25: 70 |  |  |  | Complying | Complying |  | 7.49 | 112 | 391 |  | 280 | [5 empty] | 31.54 | [13 empty] | 9300
[11 empty] | 03.06.2026 | 401, 10.06.2026 |  | 1: 7.2; 2: 7.5; 3: 32; 5: 13; 11: 4.56; 25: 63 |  |  |  | Complying | Complying |  | 7.84 | 95 | 360 |  | 205 | [5 empty] | 29.55 | [13 empty] | 7000
[11 empty] | 03.07.2026 | 281 M dt. 10.07.2026 | 191.75 | 1: 6.74; 2: 7.8; 3: 40; 5: 12; 25: 58; 52: BDL |  |  |  | Complying | Complying | 238.124 | 8.02 | 102 | 416 |  | 245 | [5 empty] | 30.84 | [13 empty] | 9300 | [26 empty] | 5.8
| July, 2nd Phase, 2026 | [9 empty] | 22.07.2026 | 390 M dt. 04.08.2026 | 247.05 | 7.03 | 8.2 | 36 |  | 18 | 1290 | 677.2 | 210 | 150 | 1.29 | 7.61 | BDL*(DL**=0.5) | 2.2 |  | 2.93 | ND |  | 19.995 | 8.126 | 32.193 |  |  | 230 | 635 | 93 |  |  | 0.82 |  |  | 0.074 | BDL*(DL**=0.0016) | 0.034 | 0.007 | BDL*(DL**=0.0008) | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.003 | 0.003 | BDL*(DL**=0.001) | 0.123 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.04 | BDL*(DL**=0.0006) | BDL*(DL***=4) |  |  | 2340 |  |  |  | Complying | Complying | 240.65 | 7.36 | 95 | 320 |  | 260 | 590 | 204.9 | 410 | 164 | 3.26 | 22.23 | 2.6 | 8.6 |  | 4.56 | 3.4 |  | 143.075 | 26.734 | 99.335 |  |  | 435 | 430 | 2900 |  |  | 3.29 |  |  | 0.137 | 0.06 | 12.703 | 0.224 | 2.2 | 0.05 | 0.105 | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.008 | 0.241 | BDL*(DL**=0.001) | 15.439 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.193 | BDL*(DL**=0.0006) | 8.2 |  |  | 1090
69 | (NUH-STP-004) 5 MLD STP Ferozpur Jhirka, Nuh, by PHED in 20.11.2019 |  | 20 | 7.00-8.00 | 100 | 40
[11 empty] | 08.01.2026 | 1943 dt. 22.01.2026 |  | 1: 7.36; 2: 5.8; 3: 32.2; 5: 13; 11: 8.4; 25: 70 |  |  |  | Complying | Complying |  | 7.72 | 82 | 346.7 |  | 190 | [5 empty] | 28.02 | [13 empty] | 5800
[11 empty] | 01.02.2026 | 2301 dt. 18.02.2026 |  | 1: 7.14; 2: 6.2; 3: 39.6; 5: 17; 11: 7.46; 25: 84 |  |  |  | Complying | Complying |  | 7.59 | 90 | 372.9 |  | 205 | [5 empty] | 34.48 | [13 empty] | 7000
[11 empty] | 13.03.2026 | 2615 dt. 25.03.2026 |  | 1: 7.23; 2: 7.4; 3: 36; 5: 15; 11: 8.44; 25: 93 |  |  |  | Complying | Complying |  | 7.84 | 102 | 416 |  | 245 | [5 empty] | 39.12 | [13 empty] | 5800
[11 empty] | 20.04.2026 | 185 dt. 30.04.2026 |  | 1: 7.36; 2: 8.2; 3: 44; 5: 17; 11: 7.12; 25: 68 |  |  |  | Complying | Complying |  | 7.64 | 112 | 448 |  | 230 | [5 empty] | 40.74 | [13 empty] | 8400
[11 empty] | 13.05.2026 | 261 dt. 20.05.2026 |  | 1: 7.33; 2: 7.2; 3: 36; 5: 15; 11: 6.68; 25: 58 |  |  |  | Complying | Complying |  | 7.52 | 115 | 392 |  | 270 | [5 empty] | 38.76 | [13 empty] | 9300
[11 empty] | 05.06.2026 | 426 dt. 18.06.2026 |  | 1: 7.6; 2: 5.2; 3: 32; 5: 11; 11: 7.12; 25: 79 |  |  |  | Complying | Complying |  | 7.51 | 102 | 408 |  | 255 | [5 empty] | 28.84 | [13 empty] | 6300
[11 empty] | 06.07.2026 | 288 M dt. 14.07.2026 |  | 1: 7.35; 2: 7.4; 3: 32; 5: 16; 25: 93; 52: BDL |  |  |  | Complying | Complying |  | 7.23 | 110 | 416 |  | 310 | [19 empty] | 7900 | [26 empty] | 8.8
| July, 2nd Phase, 2026 | [9 empty] | 22.07.2026 | 386 M dt. 04.08.2026 |  | 7.48 | 9.2 | 48 |  | 18 | 1120 | 789.6 | 290 | 83 | 1.29 | 6.24 | 2.59 | 5.6 |  | 3.09 | ND |  | 362.499 | 73.938 | 111.333 |  |  | 290 | 595 | 84 |  |  | 6.53 |  |  | 0.268 | BDL*(DL**=0.0016) | 0.146 | 0.105 | BDL*(DL**=0.0008) | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.02 | 0.004 | BDL*(DL**=0.001) | 0.079 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.047 | BDL*(DL**=0.0006) | BDL*(DL***=4) |  |  | 2040 |  |  |  | Complying | Complying |  | 7.39 | 115 | 344 |  | 275 | 750 | 489.8 | 340 | 65 | 3.64 | 21.72 | 2.69 | 4.6 |  | 4.7 | 2.4 |  | 205.029 | 0.31 | 92.083 |  |  | 340 | 490 | 7000 |  |  | 4.29 |  |  | 0.37 | 0.048 | 18.245 | 0.31 | 0.049 | 0.047 | 0.186 | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.059 | 0.244 | BDL*(DL**=0.001) | 23.769 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.268 | BDL*(DL**=0.0006) | BDL*(DL***=4) |  |  | 1350
Gurgaon South
70 | (GRS-STP-005) 50 MLD STP at Behrampur , Gurugram by GMDA in August 2010 | GMDA | <5 | 7.0 - 8.5 | <50 | Nil |  | 10 | 1 | <100
| Jan., 2026 | [9 empty] | 14.01.2026 (outlet Secondary) | 2020 dt. 28.01.2026 |  | 1: 7.51; 2: 7.4; 3: 43.8; 5: 19; 11: 8.8; 25: 93; 52: BDL*(DL**=4) |  |  |  | Complying | Complying |  | 7.44 | 120 | 462.1 |  | 235 | [5 empty] | 49.24 | [13 empty] | 13000 | [26 empty] | 8.8
[11 empty] | 14.01.2026 (outlet Teritary) | 2020 dt. 28.01.2026 |  | 1: 7.23; 2: 6.8; 3: 35.8; 5: 16; 11: 7; 25: 88; 52: BDL*(DL**=4) |  |  |  | Complying | Complying |  | 7.44 | 120 | 462.1 |  | 235 | [5 empty] | 49.24 | [13 empty] | 13000 | [26 empty] | 8.8
| Feb.,2026 | [9 empty] | 16.02.2026 (outlet Secondary) | 2353 dt. 23.02.2026 |  | 1: 7.62; 2: 7.2; 3: 40; 5: 18; 11: 8.4; 25: 79; 52: BDL*(DL**=4) |  |  |  | Complying | Complying |  | 7.49 | 110 | 396 |  | 220 | [5 empty] | 30.32 | [13 empty] | 9300 | [26 empty] | 10.6
[11 empty] | 16.02.2026 (outlet Teritary) | 2353 dt. 23.02.2026 |  | 1: 7.64; 2: 4.8; 3: 28; 5: 13; 11: 5.6; 25: 58; 52: BDL*(DL**=4) |  |  |  | Complying | Complying
| Mar.,2026 | [9 empty] | 10.03.2026 (outlet Secondary) | 2574 dt. 20.03.2026 | - | 1: 2.79; 2: 12; 3: 56; 5: 26; 11: 9.84; 25: 280; 52: BDL*(DL**=4) |  |  |  | Non complying | Non complying | 1654.9 | 7.67 | 98 | 408 |  | 290 | [5 empty] | 34.92 | [13 empty] | 8800 | [26 empty] | 9.4
[11 empty] | 10.03.2026 (outlet Teritary) | 2574 dt. 20.03.2026 | - | 1: 2.88; 2: 7.6; 3: 32; 5: 12; 11: 4.12; 25: 58; 52: BDL*(DL**=4) |  |  |  | Complying | Complying | 1654.9 | 7.67 | 98 | 408 |  | 290 | [5 empty] | 34.92 | [13 empty] | 8800 | [26 empty] | 9.4
| Apr.,2026 | [9 empty] | 15.04.2026 (outlet Secondary) | 146 dt. 28.04.2026 |  | 1: 6.28; 2: 13; 3: 64; 5: 27; 11: 8.12; 25: 490; 52: BDL*(DL**=4) |  |  |  | Non complying | Non complying |  | 8.04 | 110 | 456 |  | 305 | [5 empty] | 40.24 | [13 empty] | 8400 | [26 empty] | 10.4
[11 empty] | 15.04.2026 (outlet Tert) | 146 dt. 28.04.2026 |  | 1: 7.06; 2: 7.4; 3: 40; 5: 18; 11: 6.26; 25: 58; 52: BDL*(DL**=4) |  |  |  | Complying | Complying
[11 empty] | 13.05.2026 (outlet Secondary) | 175-176-177 dt. 23.05.2026 |  | 1: 7.8; 2: 28; 3: 160; 5: 33; 11: 11; 25: 56 |  |  |  | Non complying | Non complying |  | 7.6 | 115 | 568 |  | 318 | [5 empty] | 17 | [13 empty] | 72000
[11 empty] | 13.05.2026 (outlet Tert) | 175-176-177 dt. 23.05.2026 |  | 1: 8; 2: 16; 3: 104; 5: 18; 11: 6; 25: 45 |  |  |  | Non complying | Non complying |  | 7.6 | 115 | 568 |  | 318 | [5 empty] | 17 | [13 empty] | 72000
| June, 2026 | [9 empty] | 09.06.2026 (outlet Secondary) | 635-636-637 dt. 18.06.2026 |  | 1: 7.5; 2: 8; 3: 44; 5: 16; 11: 3; 25: 86; 55: 1160 |  |  |  | Complying | Complying |  | 7 | 100 | 368 |  | 284 | [5 empty] | 16 | [13 empty] | 84000 | [29 empty] | 1350
[11 empty] | 09.06.2026 (outlet Tertiary) | 635-636-637 dt. 18.06.2026 |  | 1: 7.6; 2: 5; 3: 32; 5: 12; 11: BDL; 25: 64; 55: 1010 |  |  |  | Complying | Complying
[11 empty] | 06.07.2026 (outlet Secondary) | 856-857-858 dt. 16.07.2026 |  | 1: 7.7; 2: 7; 3: 36; 5: 14; 11: 2.8; 14: 0.5; 25: 86; 55: 826 |  |  |  | Complying | Complying |  | 7.2 | 85 | 432 | [7 empty] | 14 |  |  | 3.6 | [10 empty] | 56000 | [29 empty] | 1040
[11 empty] | 06.07.2026 (outlet Tert) | 856-857-858 dt. 16.07.2026 |  | 1: 7.8; 2: 4; 3: 24; 5: 11; 11: BDL; 14: BDL; 25: 58; 55: 821 |  |  |  | Complying | Complying |  | 7.2 | 85 | 432 | [7 empty] | 14 |  |  | 3.6 | [10 empty] | 56000 | [29 empty] | 1040
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 (outlet Secondary) | 1072-1073-1074 dt. 30.07.2026 |  | 1: 6; 2: 14; 3: 56; 5: 30; 6: 1430; 9: 130; 10: 0.9; 11: BDL; 12: ND; 13: ND; 14: BDL; 15: ND; 16: ND; 17: ND; 19: 60; 20: 80; 24: 140; 25: 83; 28: ND; 31: ND; 33: ND; 35: ND; 36: ND; 42: ND; 52: BDL; 55: 2860 |  |  |  | Non complying | Non complying |  | 6.5 | 90 | 376 |  | 214 | 635 |  |  | 390 | 1.2 | 23 | 9.4 | 0.8 | 1.5 | 3.2 | ND | ND |  | 140 | 300 |  |  |  | 440 | 73000 |  |  | ND |  |  | ND |  | ND |  | ND | ND | [5 empty] | ND | [9 empty] | 15 |  |  | 1267
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 (outlet Tertiary) | 1072-1073-1074 dt. 30.07.2026 |  | 1: 6.1; 2: 7; 3: 40; 5: 12; 6: 1310; 9: 110; 10: 0.8; 11: BDL; 12: ND; 13: ND; 14: BDL; 15: ND; 16: ND; 17: ND; 19: 50; 20: 70; 24: 120; 25: 75; 28: ND; 31: ND; 33: ND; 35: ND; 36: ND; 42: ND; 52: BDL; 55: 2620 |  |  |  | Complying | Complying |  | 6.5 | 90 | 376 |  | 214 | 635 |  |  | 390 | 1.2 | 23 | 9.4 | 0.8 | 1.5 | 3.2 | ND | ND |  | 140 | 300 |  |  |  | 440 | 73000 |  |  | ND |  |  | ND |  | ND |  | ND | ND | [5 empty] | ND | [9 empty] | 15 |  |  | 1267
71 | (GRS-STP-006) 120 MLD STP at Behrampur , Gurugram by GMDA in July 2014 | 30% | <10 | 7.0 - 8.5 | <100 | <20
[11 empty] | 14.01.2026 (outlet Secondary) | 2019 dt. 28.01.2026 |  | 1: 7.05; 2: 8.6; 3: 39.8; 5: 18; 11: 9.8; 25: 88 |  |  |  | Complying | Complying |  | 7.21 | 95 | 422.3 |  | 240 | [5 empty] | 49.24 | [13 empty] | 11000
[11 empty] | 14.01.2026 (outlet Tertiary) | 2019 dt. 28.01.2026 |  | 1: 7.34; 2: 4.8; 3: 27.8; 5: 11; 11: 4.84; 25: 56 |  |  |  | Complying | Complying |  | 7.21 | 95 | 422.3 |  | 240 | [5 empty] | 49.24 | [13 empty] | 11000
[11 empty] | 16.02.2026 (outlet Secondary) | 2352 dt. 24.02.2026 |  | 1: 7.37; 2: 7.6; 3: 48; 5: 16; 11: 7.12; 25: 93 |  |  |  | Complying | Complying |  | 7.26 | 110 | 465 |  | 265 | [5 empty] | 36.54 | [13 empty] | 13000
[11 empty] | 16.02.2026 (outlet Tertiary) | 2352 dt. 24.02.2026 |  | 1: 7.45; 2: 5.2; 3: 32; 5: 12; 11: 6.68; 25: 49 |  |  |  | Complying | Complying |  | 7.26 | 110 | 465 |  | 265 | [5 empty] | 36.54 | [13 empty] | 13000
[11 empty] | 10.03.2026 (outlet Secondary) | 2575 dt. 20.03.2026 |  | 1: 4.76; 2: 13; 3: 60; 5: 29; 11: 3.72; 25: 330 |  |  |  | Non complying | Non complying |  | 7.96 | 120 | 484 |  | 310 | [5 empty] | 12.4 | [13 empty] | 11000
[11 empty] | 10.03.2026 (outlet Tertiary) | 2575 dt. 20.03.2026 |  | 1: 5.81; 2: 7.2; 3: 36; 5: 13; 11: 3.72; 25: 63 |  |  |  | Complying | Complying |  | 7.96 | 120 | 484 |  | 310 | [5 empty] | 12.4 | [13 empty] | 11000
| April,2026 | [9 empty] | 15.04.2026 (outlet Secondary) | 146 dt. 28.04.2026
[11 empty] | 15.04.2026 (outlet Tert) | 146 dt. 28.04.2026
[11 empty] | 13.05.2026 (outlet Secondary) | 178-179-180 dt. 23.05.2026 |  | 1: 7.7; 2: 18; 3: 104; 5: 12; 11: 8; 25: 3200 |  |  |  | Non complying | Non complying |  | 6.5 | 105 | 512 |  | 182 | [5 empty] | 15 | [13 empty] | 167000
[11 empty] | 13.05.2026 (outlet Tertiary) | 178-179-180 dt. 23.05.2026 |  | 1: 8.1; 2: 8; 3: 48; 5: 6; 11: 4; 25: 44 |  |  |  | Complying | Complying |  | 6.5 | 105 | 512 |  | 182 | [5 empty] | 15 | [13 empty] | 167000
[11 empty] | 09.06.2026 (outlet Secondary) | 638-639-640 dt. 18.06.2026 |  | 1: 7.1; 2: 7; 3: 40; 5: 16; 11: BDL; 25: 84 |  |  |  | Complying | Complying |  | 6.8 | 95 | 332 |  | 246 | [5 empty] | 14 | [13 empty] | 72000
[11 empty] | 09.06.2026 (outlet Tertiary) | 638-639-640 dt. 18.06.2026 |  | 1: 7.2; 2: 6; 3: 36; 5: 12; 11: BDL; 25: 78 |  |  |  | Complying | Complying |  | 6.8 | 95 | 332 |  | 246 | [5 empty] | 14 | [13 empty] | 72000
| July, 2026 1st Phase | [9 empty] | 06.07.2026 (outlet Secondary) | 849-850-851 dt. 16.07.2026 |  | 1: 8; 2: 6; 3: 32; 5: 18; 11: BDL; 25: 76; 55: 904 |  |  |  | Complying | Complying |  | 8.1 | 75 | 312 |  | 198 | [5 empty] | 18 | [13 empty] | 84000 | [29 empty] | 1006
| July, 2026 1st Phase | [9 empty] | 06.07.2026 (outlet Tertiary) | 849-850-851 dt. 16.07.2026 |  | 1: 7.8; 2: 5; 3: 28; 5: 16; 11: BDL; 25: 68; 55: 963 |  |  |  | Complying | Complying |  | 8.1 | 75 | 312 |  | 198 | [5 empty] | 18 | [13 empty] | 84000 | [29 empty] | 1006
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 (outlet Secondary) | 1069-1070-1071 dt. 30.07.2026 |  | 1: 5.7; 2: 12; 3: 56; 5: 30; 6: 530; 9: 150; 10: BDL; 11: BDL; 12: ND; 13: ND; 14: BDL; 15: ND; 16: ND; 17: ND; 19: 50; 20: 80; 24: 130; 25: 83; 28: ND; 31: ND; 33: ND; 35: ND; 36: ND; 42: ND; 52: BDL; 55: 1090 |  |  |  | Non complying | Non complying |  | 7.3 | 75 | 316 |  | 240 | 560 |  |  | 395 | 0.4 | 16 | 10.2 | 1.2 | 0.5 | 3.4 | ND | ND |  | 120 | 290 |  |  |  | 410 | 134000 |  |  | ND |  |  | ND |  | ND |  | ND | ND | [5 empty] | ND | [9 empty] | 15 |  |  | 1120
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 (outlet Tertiary) | 1069-1070-1071 dt. 30.07.2026 |  | 1: 6; 2: 6; 3: 32; 5: 9; 6: 520; 9: 130; 10: BDL; 11: BDL; 12: ND; 13: ND; 14: BDL; 15: ND; 16: ND; 17: ND; 19: 45; 20: 75; 24: 110; 25: 77; 28: ND; 31: ND; 33: ND; 35: ND; 36: ND; 42: ND; 52: BDL; 55: 1060 |  |  |  | Complying | Complying |  | 7.3 | 75 | 316 |  | 240 | 560 |  |  | 395 | 0.4 | 16 | 10.2 | 1.2 | 0.5 | 3.4 | ND | ND |  | 120 | 290 |  |  |  | 410 | 134000 |  |  | ND |  |  | ND |  | ND |  | ND | ND | [5 empty] | ND | [9 empty] | 15 |  |  | 1120
| August, 1st Phase | [9 empty] | 07.08.2026 (outlet Secondary) | 1445-1446-1447 dt. 18.08.2026 |  | 1: 7.1; 2: 11; 3: 32; 5: 46; 6: 745; 9: 108; 10: BDL; 11: 3.5; 12: 0.7; 13: BDL; 14: 1.1; 15: 0.8; 16: BDL; 17: BDL; 19: 55; 20: 75; 24: 145; 25: 116; 28: BDL; 31: BDL; 33: BDL; 35: BDL; 36: BDL; 42: BDL; 52: BDL; 55: 1470 |  |  |  | Non complying | Non complying |  | 6.9 | 65 | 316 |  | 310 | 760 |  |  | 224 | BDL | 27.5 | 11.4 | 8.5 | 3.8 | 3.2 | BDL | BDL |  | 80 | 110 |  |  |  | 216 | 73000 |  |  | 14.2 |  |  | BDL |  | BDL |  | BDL | BDL | [5 empty] | BDL | [9 empty] | 16 |  |  | 1590
| August, 1st Phase | [9 empty] | 07.08.2026 (outlet Tertiary) | 1445-1446-1447 dt. 18.08.2026 |  | 1: 7.5; 2: 7; 3: 28; 5: 16; 6: 690; 9: 96; 10: BDL; 11: BDL; 12: BDL; 13: BDL; 14: 0.3; 15: BDL; 16: BDL; 17: BDL; 19: 40; 20: 60; 24: 110; 25: 65; 28: BDL; 31: BDL; 33: BDL; 35: BDL; 36: BDL; 42: BDL; 52: BDL; 55: 1350 |  |  |  | Complying | Complying |  | 6.9 | 65 | 316 |  | 310 | 760 |  |  | 224 | BDL | 27.5 | 11.4 | 8.5 | 3.8 | 3.2 | BDL | BDL |  | 80 | 110 |  |  |  | 216 | 73000 |  |  | 14.2 |  |  | BDL |  | BDL |  | BDL | BDL | [5 empty] | BDL | [9 empty] | 16 |  |  | 1590
72 | 1 MLD STP, Gadoli Kalan, Gurugram South by ULB in 28.02.2021 | [9 empty] | 12.06.2026 | 679-680 dt. 19.06.2026 |  | 1: 7.3; 2: 8; 3: 48; 5: 17; 25: 92; 52: BDL |  |  |  | Complying | Complying |  | 6.5 | 95 | 352 |  | 282 | [19 empty] | 76000 | [26 empty] | 15
| July, 2026 1st Phase | [9 empty] | 06.07.2026 | 835-836 dt. 15.07.2026 |  | 1: 8; 2: 20; 3: 72; 5: 48; 11: 5; 14: 0.8; 25: 780; 52: BDL; 55: 1380 |  |  |  | Non complying | Non complying |  | 6.8 | 105 | 492 |  | 182 | [5 empty] | 29 |  |  | 1.5 | [10 empty] | 76000 | [26 empty] | 18 |  |  | 1485
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | 1103-1104 dt. 30.07.2026 |  | 1: 7.3; 2: 5; 3: 36; 5: 11; 6: 680; 9: 140; 10: ND; 11: 4.5; 12: ND; 13: ND; 14: 0.5; 15: ND; 16: ND; 17: ND; 19: 40; 20: 70; 24: 110; 25: 71; 28: ND; 31: ND; 33: ND; 35: ND; 36: ND; 42: ND; 52: BDL; 55: 1350 |  |  |  | Complying | Complying |  | 6.7 | 110 | 424 |  | 282 | 869 |  |  | 340 | ND | 23 | 8.4 | 1.1 | 1 | 3.2 | ND | ND |  | 1501 | 290 |  |  |  | 440 | 114000 |  |  | ND |  |  | ND |  | ND |  | ND | ND | [5 empty] | ND | [9 empty] | 15 |  |  | 1737
[11 empty] | 06.08.2026 | 1450-1451 dt. 18.08.2026 |  | 1: 7.7; 2: 12; 3: 68; 5: 36; 6: 835; 9: 56; 10: BDL; 11: 0.2; 12: 0.6; 13: BDL; 14: BDL; 15: BDL; 16: BDL; 17: BDL; 19: 48; 20: 74; 24: 156; 25: 64; 28: BDL; 31: BDL; 33: BDL; 35: BDL; 36: BDL; 42: BDL; 52: BDL; 55: 1670 |  |  |  | Non complying | Non complying |  | 7.2 | 75 | 312 |  | 286 | 950 |  |  | 184 | BDL | 21 | 7.5 | 3.2 | 1.7 | 1.1 | BDL | BDL |  | 82 | 124 |  |  |  | 265 | 89000 |  |  | BDL |  |  | BDL |  | BDL |  | BDL | BDL | [5 empty] | BDL | [9 empty] | 13.5 |  |  | 1940
73 | 1 MLD STP, Darbaripur, Gurugram South by ULB in 28.02.2021
| July, 2026 1st Phase | [9 empty] | 07.07.2026 | 863-864 dt. 16.07.2026 |  | 1: 7.2; 2: 40; 3: 164; 5: 74; 11: 13; 14: 1.8; 25: 5600; 52: 12; 55: 1970 |  |  |  | Non complying | Non complying
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 1075-1076 dt. 30.07.2026 |  | 1: 7.1; 2: 5; 3: 36; 5: 12; 6: 843; 9: 120; 10: ND; 11: 5.6; 12: ND; 13: ND; 14: 0.2; 15: ND; 16: ND; 17: ND; 19: 50; 20: 70; 24: 160; 25: 58; 28: ND; 31: ND; 33: ND; 35: ND; 36: ND; 42: ND; 52: BDL; 55: 1685 |  |  |  | Complying | Complying |  | 7.3 | 70 | 348 |  | 208 | 895 |  |  | 370 | 1.2 | 21 | 7.2 | 0.9 | 3.6 | 3.1 | ND | ND |  | 155 | 325 |  |  |  | 480 | 95000 |  |  | ND |  |  | ND |  | ND |  | ND | ND | [5 empty] | ND | [9 empty] | 14 |  |  | 1790
74 | (GRN-STP-009) 2 MLD STP, Mohmadpur Jharsa, Gurugram South by ULB in 31.03.2021 | [9 empty] | 12.06.2026 | 681-682 dt. 19.06.2026 |  | 1: 7.2; 2: 7; 3: 40; 5: 14; 25: 74; 52: 14 |  |  |  | Complying | Complying |  | 6.4 | 105 | 368 |  | 240 | [19 empty] | 89000
| July, 2026 1st Phase | [9 empty] | 06.07.2026 | 837-838 dt. 15.07.2026 |  | 1: 7.9; 2: 18; 3: 64; 5: 108; 11: 15; 14: 1.4; 25: 1200; 52: BDL; 55: 2640 |  |  |  | Non complying | Non complying |  | 8.1 | 85 | 372 |  | 162 | [8 empty] | 1.9 | [10 empty] | 84000 | [26 empty] | 19 |  |  | 2600
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | 1105-1106 dt. 30.07.2026 |  | 1: 7.1; 2: 35; 3: 72; 5: 46; 6: 1165; 9: 70; 10: ND; 11: BDL; 12: ND; 13: ND; 14: BDL; 15: ND; 16: ND; 17: ND; 19: 60; 20: 90; 24: 150; 25: 1700; 28: ND; 31: ND; 33: ND; 35: ND; 36: ND; 42: ND; 52: BDL; 55: 2330 |  |  |  | Non complying | Non complying |  | 7 | 115 | 348 |  | 298 | 1350 |  |  | 260 | ND | 19 | 7.1 | 7.1 | 1.5 | 2.8 | ND | ND |  | 150 | 350 |  |  |  | 500 | 153000 |  |  | ND |  |  | ND |  | ND |  | ND | ND | [5 empty] | ND | [9 empty] | 15 |  |  | 2700
[11 empty] | 07.08.2026 | 1448-1449 dt. 18.08.2026 |  | 1: 7.1; 2: 18; 3: 72; 5: 56; 6: 750; 9: 68; 10: BDL; 11: 3.6; 12: 1.3; 13: 0.2; 14: BDL; 15: BDL; 16: BDL; 17: BDL; 19: 46; 20: 84; 24: 172; 25: 1300; 28: BDL; 31: BDL; 33: BDL; 35: BDL; 36: BDL; 42: BDL; 52: 2.4; 55: 1510 |  |  |  | Non complying | Non complying |  | 6.9 | 105 | 272 |  | 312 | 875 |  |  | 212 | BDL | 21.5 | 9.4 | 3.2 | 1.9 | 0.7 | BDL | BDL |  | 75 | 106 |  |  |  | 204 | 148000 |  |  | 4.7 |  |  | BDL |  | BDL |  | BDL | BDL | [5 empty] | BDL | [9 empty] | 12.5 |  |  | 1740
75 | 25 MLD, Manesar and Naharpur Kasan, Gurugram, GMDA 31.08.2025
| July, 2026 1st Phase | [9 empty] | 06.07.2026 | 833-834 dt. 15.07.2026 |  | 1: 8.5; 2: 8; 3: 44; 5: 16; 11: ND; 14: ND; 25: 56; 52: BDL; 55: 1485 |  |  |  | Complying | Complying |  | 8 | 105 | 368 |  | 182 | [8 empty] | 1.1 | [10 empty] | 62000 | [26 empty] | 16 |  |  | 1795
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | 1111-1112 dt. 30.07.2026 |  | 1: 7.5; 2: 7; 3: 36; 5: 12; 6: 420; 9: 128; 10: 0.5; 11: 5.5; 12: 2.5; 13: 6.4; 14: 1.1; 15: 0.7; 16: ND; 17: ND; 19: 48; 20: 84; 24: 140; 25: 65; 28: 5.2; 31: ND; 33: ND; 35: ND; 36: ND; 42: ND; 52: BDL; 55: 804 |  |  |  | Complying | Complying |  | 6.8 | 70 | 312 |  | 168 | 715 |  |  | 164 | 1.2 | 1.6 | 36.2 | 15.2 | 2.9 | 2.6 | 1.2 | ND |  | 90 | 270 |  |  |  | 340 | 72000 |  |  | 8.6 |  |  | ND |  | ND |  | ND | ND | [5 empty] | ND | [9 empty] | 8 |  |  | 1357
[11 empty] | 06.08.2026 | 1419-1420 dt. 14.08.2026 |  | 1: 7.5; 2: 9; 3: 44; 5: 18; 6: 670; 9: 142; 10: BDL; 11: BDL; 12: BDL; 13: BDL; 14: BDL; 15: BDL; 16: BDL; 17: BDL; 19: 70; 20: 106; 24: 176; 25: 92; 28: BDL; 31: BDL; 33: BDL; 35: BDL; 36: BDL; 42: BDL; 52: BDL; 55: 1210 |  |  |  | Complying | Complying |  | 7.2 | 110 | 324 |  | 248 | 724 |  |  | 342 | BDL | 18 | 17.2 | 19.2 | 0.9 | 2.7 | BDL | BDL |  | 70 | 106 |  |  |  | 176 | 92 |  |  | BDL |  |  | BDL |  | BDL |  | BDL | BDL | [5 empty] | BDL | [9 empty] | 13 |  |  | 1340
Faridabad
76 | (FBD-STP-001) 45 MLD STP, Badshahpur Faridabad by ULB in 1.9.2011
[11 empty] | 08.01.2026 | 1939 dt. 22.01.2026 | 103.47 | 1: 7.64; 2: 35; 3: 177.4; 5: 82; 11: 14.01; 25: 580 |  |  |  | Non complying | Non complying | 4438 | 7.64 | 110 | 411.2 |  | 82 | [5 empty] | 14.01 | [13 empty] | 580
[11 empty] | 04.02.2026 | 2230 dt. 12.02.2026 | - | 1: 7.18; 2: 28; 3: 169.3; 5: 68; 11: 11.2; 25: 330 |  |  |  | Non complying | Non complying | 400853 | 7.26 | 90 | 370.9 |  | 240 | [5 empty] | 38.54 | [13 empty] | 9300
[11 empty] | 10.03.2026 | 2570 dt. 17.03.2026 |  | 1: 7.24; 2: 9.2; 3: 48; 5: 18; 11: 9.74; 25: 84 |  |  |  | Complying | Complying |  | 7.41 | 98 | 408 |  | 225 | [5 empty] | 36.94 | [13 empty] | 9300
[11 empty] | 07.04.2026 | 46 dt. 13.04.2026 | - | 1: 8.18; 2: 8.2; 3: 44; 5: 16; 11: 8.03; 25: 78 |  |  |  | Complying | Complying | 51565.35 | 7.79 | 104 | 380 |  | 235 | [5 empty] | 42.04 | [13 empty] | 8400
[11 empty] | 19.05.2026 | 246 dt. 15.05.2026 |  | 1: 7.38; 2: 7.4; 3: 36; 5: 14; 11: 7.12; 25: 63 |  |  |  | Complying | Complying |  | 7.28 | 102 | 392 |  | 275 | [19 empty] | 5800
[11 empty] | 03.06.2026 | 403 dt. 10.06.2026 |  | 1: 7.9; 2: 13; 3: 80; 5: 19; 11: 8.48; 25: 93 |  |  |  | Non complying | Non complying |  | 7.45 | 110 | 456 |  | 250 | [5 empty] | 37.48 | [13 empty] | 7000
[11 empty] | 06.07.2026 | 301 M dt. 14.07.2026 |  | 1: 7.44; 2: 4.2; 3: 28; 5: 12; 11: 6.84; 25: 70; 52: BDL* (DL**=4); 55: 710 |  |  |  | Complying | Complying |  | 7.12 | 102 | 392 |  | 265 | [5 empty] | 32.92 | [13 empty] | 5800 | [26 empty] | 6.8 |  |  | 2850
| August, 1st Phase | [9 empty] | 07.08.2026 | 659 dt. 14.08.2026 | not working | 7.3 | 8.2 | 48 |  | 17 | 340 | 132.3 | 150 | 133 | 0.55 | 7.48 | BDL*(DL**=0.5) | 4.7 |  | 0.61 | ND |  | 111.32 | 14.3 | 23.6 |  |  | 195 | 120 | 84 |  |  | 4.46 |  |  | 0.115 | 0.002 | 0.028 | 0.026 | 0.001 | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.02 | 0.023 | BDL*(DL**=0.001) | 0.04 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.078 | BDL*(DL**=0.0006) | BDL* (DL**=4) |  |  | 620 |  |  |  | Complying | Complying | not working | 8.12 | 125 | 488 |  | 310 | 1180 | 297.4 | 320 | 150 | 1.74 | 26.42 | 3.14 | 13.2 |  | 2.46 | 1.6 |  | 278.156 | 46.6 | 76.9 |  |  | 340 | 390 | 7000 |  |  | 6.17 |  |  | 0.32 | 0.008 | 1.762 | 0.084 | 0.035 | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.035 | 0.178 | BDL*(DL**=0.001) | 1.284 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.126 | BDL*(DL**=0.0006) | 12.6 |  |  | 2150
77 | (FBD-STP-003 ) 10 MLD STP, Faridabad by ULBD in 31.03.2023 (Faridabad Smart City Limited, 11/13, Mehakma)
[11 empty] | 08.01.2026 | 1936 dt. 22.01.2026 | 7.69 | 1: 7.31; 2: 6.4; 3: 32.2; 5: 13; 11: 7; 25: 84 |  |  |  | Complying | Complying | 7.9 | 7.73 | 105 | 427.9 |  | 235 | [5 empty] | 33.12 | [13 empty] | 7000
[11 empty] | 04.02.2026 | 2238 dt. 12.02.2026 | 7.8 | 1: 7.21; 2: 6.8; 3: 36.2; 5: 18; 11: 6.84; 25: 93 |  |  |  | Complying | Complying | 7.99 | 7.46 | 90 | 362.8 |  | 270 | [5 empty] | 38.52 | [13 empty] | 7900
[11 empty] | 06.03.2026 | 2550 dt. 17.03.2026 |  | 1: 7.45; 2: 7.4; 3: 44; 5: 15; 11: 7.12; 25: 63 |  |  |  | Complying | Complying |  | 8.24 | 76 | 328 |  | 275 | [5 empty] | 36.54 | [13 empty] | 8400
[11 empty] | 07.04.2026 | 42 dt. 13.04.2026 | 6.092 | 1: 7.21; 2: 7.2; 3: 36; 5: 11; 11: 6.28; 25: 58 |  |  |  | Complying | Complying | 5.703 | 7.56 | 82 | 352 |  | 230 | [5 empty] | 42.24 | [13 empty] | 7000
[11 empty] | 18.05.2026 | 285 dt. 27.05.2026 | 4.11 | 1: 7.68; 2: 6.2; 3: 32; 5: 14; 11: 5.68; 25: 84 |  |  |  | Complying | Complying | 4.54 | 7.85 | 115 | 448 |  | 275 | [5 empty] | 36.84 | [13 empty] | 5800
[11 empty] | 08.06.2026 | 428 dt. 19.06.2026 | 3.778 | 1: 8.03; 2: 6.8; 3: 32; 5: 16; 11: 6.84; 25: 79 |  |  |  | Complying | Complying |  | 8.23 | 85 | 376 |  | 240 | [5 empty] | 30.54 | [13 empty] | 6300
[11 empty] | 03.07.2026 | 279 dt. 10.07.2026 | 4.229 | 1: 7.94; 2: 4.2; 3: 28; 5: 8; 11: 7.12; 25: 80; 52: BDL; 55: 1490 |  |  |  | Complying | Complying | 7.7 | 8.11 | 92 | 360 |  | 285 | [5 empty] | 37.26 | [13 empty] | 7900 | [29 empty] | 2120
| August, 1st Phase | [9 empty] | 05.08.2026 | 636 dt. 13.08.2026 | 9.2 | 7.71 | 5.4 | 28 |  | 7 | 1080 | 414.8 | 225 | 80 | 0.74 | 7.6 | BDL*(DL**=0.5) | 2.3 |  | 0.84 | ND |  | 372.8 | 43.25 | 71.34 |  |  | 225 | 360 | 63 |  |  | 8.58 |  |  | 0.129 | 0.022 | 0.14 | 0.01 | 0.026 | 0.017 | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | 0.001 | BDL*(DL**=0.0007) | 0.036 | 0.037 | BDL*(DL**=0.001) | 0.085 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.029 | BDL*(DL**=0.0006) | BDL* (DL**=4) |  |  | 1980 |  |  |  | Complying | Complying | 9.3 | 7.23 | 120 | 368 |  | 245 | 1120 | 420.6 | 250 | 85 | 1.05 | 24.12 | 6.48 | 9.6 |  | 2.13 | 2.4 |  | 401.164 | 45.68 | 75.35 |  |  | 250 | 378 | 7000 |  |  | 8.98 |  |  | 0.225 | 0.036 | 5.025 | 0.017 | 0.105 | 0.061 | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | 0.004 | BDL*(DL**=0.0007) | 0.035 | 0.178 | BDL*(DL**=0.001) | 1.284 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.126 | BDL*(DL**=0.0006) | 12.6 |  |  | 2150
78 | (FBD-STP-004) 30 MLD STP, Badshapur Faridabad by FMDA in 31.12.2023
[11 empty] | 08.01.2026 | 1938 dt. 22.01.2026 | - | 1: 7.24; 2: 7.4; 3: 36.2; 5: 15; 11: 7.12; 25: 84 |  |  |  | Complying | Complying | 99.89 | 6.71 | 92 | 370.9 |  | 195 | [5 empty] | 49.24 | [13 empty] | 9300
[11 empty] | 04.02.2026 | 2231 dt. 12.02.2026 | 12969 | 1: 7.28; 2: 8.2; 3: 48.3; 5: 17; 11: 6.84; 25: 93 |  |  |  | Complying | Complying | 13616 | 6.93 | 102 | 403.2 |  | 240 | [5 empty] | 48.14 | [13 empty] | 7000
[11 empty] | 10.03.2026 | 2571 dt. 17.03.2026 | 10200 | 1: 7.44; 2: 7.4; 3: 36; 5: 14; 11: 6.92; 25: 70 |  |  |  | Complying | Complying | 10231 | 8.19 | 94 | 376 |  | 250 | [5 empty] | 31.84 | [13 empty] | 8400
[11 empty] | 07.04.2026 | 45 dt. 13.04.2026 | 21615 | 1: 7.8; 2: 6.4; 3: 32; 5: 17; 11: 5.94; 25: 86 |  |  |  | Complying | Complying | 16337 | 8.45 | 106 | 396 |  | 285 | [5 empty] | 42.36 | [13 empty] | 7200
[11 empty] | 08.05.2026 | 245 dt. 15.05.2026 | 21410 | 1: 7.08; 2: 9.4; 3: 48; 5: 18; 11: 6.64; 25: 79 |  |  |  | Complying | Complying
[11 empty] | 03.06.2026 | 402 dt. 10.06.2026 | 20407 | 1: 8.12; 2: 7.4; 3: 44; 5: 14; 11: 7.12; 25: 89 |  |  |  | Complying | Complying |  | 8.04 | 95 | 392 |  | 310 | [5 empty] | 43.14 | [13 empty] | 9300
[11 empty] | 06.07.2026 | 300 M dt. 14.07.2026 | 17855 | 1: 7; 2: 5.6; 3: 32; 5: 10; 11: 7.02; 25: 63; 52: BDL* (DL**=4); 55: 730 |  |  |  | Complying | Complying | 18963 | 7.48 | 105 | 408 |  | 275 | [5 empty] | 38.12 | [13 empty] | 8400 | [26 empty] | 6.8 |  |  | 3090
| August, 1st Phase | [9 empty] | 07.08.2026 | 658 dt. 14.08.2026 | 19867 | 7.34 | 6.8 | 40 |  | 14 | 1020 | 374.8 | 220 | 72 | 0.74 | 6.48 | 0.74 | 2.8 |  | BDL*(DL**=0.4) | ND |  | 205.118 | 40.09 | 66.8 |  |  | 240 | 336 | 63 |  |  | 4.91 |  |  | 0.039 | 0.04 | 0.019 | 0.011 | BDL*(DL**=0.0008) | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.019 | 0.018 | BDL*(DL**=0.001) | 0.04 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.079 | BDL*(DL**=0.0006) | BDL* (DL**=4) |  |  | 1870 |  |  |  | Complying | Complying | 20939 | 7.81 | 92 | 376 |  | 310 | 1790 | 449.8 | 460 | 104 | 4.26 | 30.82 | 6.16 | 16.4 |  | 3.39 | 2.8 |  | 420.203 | 69.4 | 114.6 |  |  | 490 | 580 | 4900 |  |  | 7.64 |  |  | 0.104 | 0.051 | 2.028 | 0.106 | 0.009 | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.724 | 0.105 | BDL*(DL**=0.001) | 2.116 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.105 | BDL*(DL**=0.0006) | 10.8 |  |  | 3270
79 | (FBD-STP-005) 2 MLD STP at Dushera ULBD in 31.08.2024 | [9 empty] | 07.04.2026 | 44 dt. 13.04.2026 |  | 1: 7.65; 2: 6.2; 3: 48; 5: 18; 11: 10.17; 25: 84 |  |  |  | Complying | Complying |  | 8.4 | 102 | 416 |  | 265 | [5 empty] | 48.43 | [13 empty] | 6300
[11 empty] | 19.05.2026 | 293 dt. 27.05.2026 |  | 1: 7.31; 2: 7.4; 3: 40; 5: 15; 11: 9.56; 25: 70 |  |  |  | Complying | Complying |  | 7.92 | 95 | 392 |  | 280 | [5 empty] | 31.96 | [13 empty] | 5800
[11 empty] | 08.06.2026 | 429 dt. 19.06.2026 |  | 1: 8.1; 2: 8.2; 3: 44; 5: 17; 11: 8.42; 25: 84 |  |  |  | Complying | Complying |  | 8.45 | 88 | 376 |  | 210 | [5 empty] | 28.02 | [13 empty] | 6300
[11 empty] | 03.07.2026 | 278 M dt. 10.07.2026 |  | 1: 7.76; 2: 5.4; 3: 32; 5: 18; 11: 5.68; 25: 63; 52: BDL* (DL**=4); 55: 1220 |  |  |  | Complying | Complying |  | 7.16 | 110 | 448 |  | 255 | [5 empty] | 31.44 | [13 empty] | 5800 | [26 empty] | 7.2 |  |  | 2630
| August, 1st Phase | [9 empty] | 07.08.2026 | 662 dt. 17.08.2026 |  | 7.68 | 8.2 | 48 |  | 14 | 640 | 294.8 | 220 | 76 | 0.55 | 4.38 | 1.06 | 2.3 |  | 1.93 | ND |  | 182.723 | 49.8 | 82.1 |  |  | 270 | 412 | 79 |  |  | 3.93 |  |  | 0.07 | 0.002 | 0.006 | BDL*(DL**=0.0002) | BDL*(DL**=0.0008) | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.023 | BDL*(DL**=0.0009) | BDL*(DL**=0.001) | 0.004 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.042 | BDL*(DL**=0.0006) | BDL* (DL**=4) |  |  | 1160 |  |  |  | Complying | Complying |  | 7.07 | 145 | 536 |  | 185 | 1330 | 579.2 | 350 | 110 | 2.06 | 30.82 | 5.28 | 11.6 |  | 5.08 | 2.4 |  | 376.129 | 53.46 | 88.17 |  |  | 390 | 448 | 5800 |  |  | 7.34 |  |  | 0.195 | 0.008 | 1.025 | 0.015 | 0.012 | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.42 | BDL*(DL**=0.0009) | BDL*(DL**=0.001) | 0.004 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.042 | BDL*(DL**=0.0006) | BDL* (DL**=4) |  |  | 2410
80 | (FBD-STP-006) 5 MLD at Golf Course ULBD in 30.09.2024
[11 empty] | 08.01.2026 | 1937 dt. 22.01.2026 | - | 1: 7.33; 2: 8.6; 3: 44.4; 5: 19; 11: 8.4; 25: 63 |  |  |  | Complying | Complying | 4.05 | 7.49 | 82 | 322.2 |  | 260 | [5 empty] | 39.22 | [13 empty] | 4900
[11 empty] | 04.02.2026 | 2237 dt. 12.02.2026 | 4.31 | 1: 7.38; 2: 7.4; 3: 40.3; 5: 16; 11: 7; 25: 84 |  |  |  | Complying | Complying | 4.61 | 8.11 | 102 | 419.3 |  | 225 | [5 empty] | 31.64 | [13 empty] | 5800
[11 empty] | 10.03.2026 | 2576 dt. 21.03.2026 | 3.88 | 1: 6.9; 2: 6.2; 3: 32; 5: 15; 11: 5.6; 25: 93 |  |  |  | Complying | Complying | 4.02 | 7.43 | 108 | 424 |  | 270 | [5 empty] | 39.72 | [13 empty] | 7900
Apr., 2026
[11 empty] | 08.05.2026 | 247 dt. 15.05.2026 | 4.18 | 1: 7.27; 2: 6; 3: 44; 5: 18; 11: 7.4; 25: 84 |  |  |  | Complying | Complying | 4.53 | 6.95 | 125 | 488 |  | 310 | [5 empty] | 44.68 | [13 empty] | 9300
[11 empty] | 08.06.2026 | 427 dt. 19.06.2026 | 4.51 | 1: 7.48; 2: 5.8; 3: 36; 5: 15; 11: 8.72; 25: 93 |  |  |  | Complying | Complying | 4.71 | 7.85 | 110 | 424 |  | 285 | [5 empty] | 39.14 | [13 empty] | 7000
[11 empty] | 03.07.2026 | 277 dt. 10.07.2026 | 4.41 | 1: 7.22; 2: 7; 3: 44; 5: 11; 11: 7.24; 25: 79; 52: BDL* (DL**=4); 55: 1190 |  |  |  | Complying | Complying | 4.61 | 7.13 | 98 | 392 |  | 255 | [5 empty] | 32.24 | [13 empty] | 8400 | [26 empty] | 6.8 |  |  | 2460
| August, 1st Phase | [9 empty] | 07.08.2026 | 657 dt. 14.08.2026 | 4.32 | 7.42 | 4.6 | 24 |  | 5 | 530 | 374.6 | 160 | 103 | 0.45 | 5.6 | 0.56 | 3.7 |  | 0.46 | ND |  | 312.238 | 29.6 | 48.8 |  |  | 225 | 240 | 49 |  |  | 8.7 |  |  | 0.112 | 0.002 | 0.159 | 0.022 | BDL*(DL**=0.0008) | BDL*(DL**=0.002) | 0.003 | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.019 | 0.011 | BDL*(DL**=0.001) | 0.087 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.039 | BDL*(DL**=0.0006) | BDL* (DL**=4) |  |  | 960 |  |  |  | Complying | Complying | 4.52 | 7.57 | 120 | 392 |  | 310 | 1370 | 422.3 | 340 | 115 | 1.95 | 26.12 | 4.48 | 11.2 |  | 2.26 | 1.2 |  | 447.116 | 55.6 | 91.7 |  |  | 340 | 460 | 7000 |  |  | 9.08 |  |  | 0.22 | 0.018 | 7.115 | 0.31 | 0.079 | 0.031 | 0.158 | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.136 | 0.328 | BDL*(DL**=0.001) | 9.084 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.106 | BDL*(DL**=0.0006) | BDL* (DL**=4) |  |  | 2490
Ballabgarh
81 | (FBD-STP-006) 15 MLD at Partapgarh Sector-25 Faridabad (FSCL) Ballabgarh | [9 empty] | 22.05.2026 | 330 dt. 01.06.2026 |  | 1: 7.4; 2: 4.5; 3: 20; 5: 5; 11: 6.12; 25: 58 |  |  |  | Complying | Complying |  | 7.2 | 94 | 360 |  | 275 | [5 empty] | 28.02 | [13 empty] | 4900
[11 empty] | 05.06.2026 | 413 dt. 16.06.2026 |  | 1: 8.38; 2: 7.5; 3: 36; 5: 8; 11: 5.6; 25: 63 |  |  |  | Complying | Complying |  | 7.18 | 90 | 352 |  | 230 | [5 empty] | 33.16 | [13 empty] | 7000
82 | (BLB-STP-003) 100 MLD STP Partapgarh , Ballabgarh by ULBD in 31.03.2024
[11 empty] | 02.01.2026 | 1858 dt. 09.01.2026 |  | 1: 7.75; 2: 8.2; 3: 40; 5: 16 |  |  |  | Complying | Complying
[11 empty] | 18.02.2026 | 2433 dt. 03.03.2026 |  | 1: 7.12; 2: 7.2; 3: 36; 5: 12 |  |  |  | Complying | Complying |  | 6.18 | 82 | 344 |  | 230
[11 empty] | 27.03.2026 | 2689 dt. 03.04.2026 |  | 1: 7.15; 2: 11; 3: 56; 5: 29 |  |  |  | Non Complying | Non Complying
[11 empty] | 23.04.2026 | 201 dt. 05.05.2026 | 69.3 | 1: 7.31; 2: 13; 3: 80; 5: 27; 11: 12.6; 25: 190 |  |  |  | Non Complying | Non Complying | 70.3 | 6.96 | 110 | 488 |  | 280 | [5 empty] | 32.34 | [13 empty] | 8400
[11 empty] | 20.05.2026 | 300 dt. 29.05.2026 | 38 | 1: 7.42; 2: 12; 3: 68; 5: 18; 11: 11.84; 25: 150 |  |  |  | Non Complying | Non Complying | 40 | 6.84 | 125 | 520 |  | 275 | [5 empty] | 30.82 | [13 empty] | 9300
[11 empty] | 05.06.2026 | 412 dt. 16.06.2026 | 14.7 | 1: 7.55; 2: 9.8; 3: 60; 5: 15; 11: 7.26; 25: 180 |  |  |  | Non Complying | Non Complying | 27.6 | 7.02 | 110 | 448 |  | 310 | [5 empty] | 34.12 | [13 empty] | 8400
83 | (BLB-STP-004) 80 MLD STP Mirjapur , Ballabgarh by ULBD in 31.03.2024
[11 empty] | 14.01.2026 | 2033 dt. 28.01.2026 |  | 1: 7.21; 2: 7.4; 3: 35.8; 5: 16 |  |  |  | complying | complying
[11 empty] | 07.02.2026 | 2284 dt. 16.02.2026 |  | 1: 7.19; 2: 13; 3: 67.4; 5: 23 |  |  |  | Non Complying | Non Complying
[11 empty] | 07.03.2026 | 2551 dt. 17.03.2026 |  | 1: 7.12; 2: 13; 3: 60; 5: 27 |  |  |  | Non Complying | Non Complying
[11 empty] | 08.04.2026 | 84 dt. 17.04.2026 |  | 1: 8.22; 2: 7.2; 3: 40; 5: 14 |  |  |  | complying | complying
[11 empty] | 22.05.2026 | 326 dt. 01.06.2026 | 55.347 | 1: 7.88; 2: 5.6; 3: 20; 5: 12; 11: 7.12; 25: 79 |  |  |  | complying | complying | 53.484 | 8.05 | 110 | 384 |  | 320 | [5 empty] | 31.72 | [13 empty] | 7900
[11 empty] | 02.06.2026 | 394 dt. 10.06.2026 | 44.243 | 1: 7.36; 2: 8.8; 3: 36; 5: 15; 11: 9.63; 25: 93 |  |  |  | complying | complying | 46.905 | 7.11 | 105 | 488 |  | 240 | [5 empty] | 34.12 | [13 empty] | 8400
84 | (BLB-STP-002 ) 7.5 MLD STP, Ballabgarh by HSVP in 31.03.2021
[11 empty] | 14.01.2026 | 2032 dt. 28.01.2026 |  | 1: 7.09; 2: 6.8; 3: 31.8; 5: 18 |  |  |  | complying | complying
[11 empty] | 10.02.2026 | 2300 dt. 18.02.2026 |  | 1: 7.08; 2: 7.4; 3: 39.6; 5: 15 |  |  |  | complying | complying
[11 empty] | 03.03.2026 | 2511 dt. 12.03.2026 |  | 1: 7.34; 2: 7.2; 3: 44; 5: 17 |  |  |  | complying | complying
[11 empty] | 27.04.2026 | 209 dt. 05.05.2026 | 1.653 | 1: 7.39; 2: 8.4; 3: 32; 5: 16; 11: 4.12; 25: 79 |  |  |  | complying | complying | 1.974 | 6.64 | 110 | 456 |  | 275 | [5 empty] | 31.39 | [13 empty] | 9300
[11 empty] | 22.05.2026 | 327 dt. 01.06.2025 | 1920 | 1: 7.25; 2: 7.2; 3: 40; 5: 14; 11: 6.18; 25: 84 |  |  |  | complying | complying | 1995 | 7.35 | 105 | 408 |  | 210 | [5 empty] | 36.92 | [13 empty] | 7000
[11 empty] | 02.06.2026 | 394 dt. 10.06.2026 | 1.8796 | 1: 8.23; 2: 14; 3: 68; 5: 27; 11: 8.45; 25: 150 |  |  |  | Non complying | Non complying | 1.387 | 7.16 | 110 | 456 |  | 270 | [5 empty] | 37.34 | [13 empty] | 8400
Palwal
85 | (PWL-STP-001) 3 MLD STP Hassanpur Palwal by PHED in 1.3.2016 (MBBR+dual filter) |  | 10 | 5.5-9.0 | 100 | 10
[11 empty] | 06.01.2026 | 1903 dt. 16.01.2026 |  | 1: 8.26; 2: 72; 3: 304; 5: 160; 11: 18.21; 25: 580 |  |  |  | Non complying | Non complying
[11 empty] | 06.02.2026 | 2280 dt. 14.02.2026 |  | 1: 7.12; 2: 84; 3: 346.7; 5: 175; 11: 18.21; 25: 840 |  |  |  | Non complying | Non complying
[11 empty] | 10.03.2026 | 2573 dt. 20.02.2026 |  | 1: 7.35; 2: 55; 3: 284; 5: 165; 11: 15.96; 25: 780 |  |  |  | Non complying | Non complying
[11 empty] | 08.04.2026 | 89 dt. 17.04.2026 |  | 1: 7.53; 2: 15; 3: 64; 5: 39; 11: 18.61; 25: 580 |  |  |  | Non complying | Non complying |  | 8.24 | 110 | 448 |  | 240 | [5 empty] | 38.72 | [13 empty] | 9300
[11 empty] | 04.05.2026 | 229 dt.12.05.2026 (Bypass) |  | 1: 7.38; 2: 115; 3: 472; 5: 290; 11: 20.12; 25: 1100 |  |  |  | Non complying | Non complying
[11 empty] | 02.06.2026 | 396 dt. 10.06.2026 |  | 1: 8.41; 2: 14; 3: 60; 5: 32; 11: 13.46; 25: 390 |  |  |  | Non complying | Non complying |  | 7.44 | 110 | 456 |  | 275 | [5 empty] | 34.12 | [13 empty] | 8400
| 1st Phase July, 2026 | [9 empty] | 06.07.2026 | 292 M dt. 14.07.2026 | - | 1: 8.33; 2: 12; 3: 60; 5: 24; 11: 13.84; 25: 420; 52: BDL*(DL**=4); 55: 1660 |  |  |  | Non-Complying | Non-Complying | 630.18 | 7.02 | 104 | 416 |  | 290 | [5 empty] | 30.84 | [13 empty] | 7000 | [26 empty] | 8.2
| 2nd Phase July, 2026 | [9 empty] | 20.07.2026 | 362 M dt. 29.07.2026 |  | 7.55 | 12 | 56 | BDL*(DL**=4) | 17 | 980 | 424.8 | 11 | 125 | 0.78 | 8.44 | 2.16 | 5.61 |  | 1.53 | ND |  | 411.677 | 59.315 | 77.764 |  |  | 100 | 450 | 93 |  |  | 8.56 |  |  | 0.224 | BDL*(DL**=0.0004) | 0.031 | 0.045 | BDL*(DL**=0.0002) | BDL*(DL**=0.0005) | BDL*(DL**=0.001) | BDL*(DL**=0.001) | BDL*(DL**=0.0001) | BDL*(DL**=0.0002) | 0.018 | 0.003 | BDL*(DL**=0.001) | 0.054 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.053 | BDL*(DL**=0.0006) | BDL*(DL**=4) |  |  | 1790 |  |  |  | Non-Complying | Non-Complying |  | 7.52 | 102 | 312 |  | 205 | 1750 | 692.2 | 340 | 119 | 2.45 | 19.85 | 4.76 | 2.56 |  | 3.8 | 1.2 |  | 514.083 | 78.401 | 107.337 |  |  | 520 | 730 | 6300 |  |  | 9.2 |  |  | 0.236 | BDL*(DL**=0.0004) | 4.753 | 0.758 | 0.018 | 0.019 | BDL*(DL**=0.001) | BDL*(DL**=0.001) | BDL*(DL**=0.0001) | BDL*(DL**=0.0002) | 0.084 | 0.054 | BDL*(DL**=0.001) | 7.312 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.195 | BDL*(DL**=0.0006) | BDL*(DL**=4) |  |  | 3180
[11 empty] | 06.08.2026 | 640 dt. 13.08.2026 | Not working | 7.17 | 13 | 64 | BDL*(DL**=4) | 29 | 860 | 294.9 | 110 | 110 | 0.63 | 7.4 | BDL*(DL**=0.5) | 2.3 |  | 0.44 | ND |  | 319.158 | 31.83 | 52.5 |  |  | 355 | 270 | 170 |  |  | 8.3 |  |  | 0.214 | BDL*(DL**=0.0016) | 0.024 | 0.014 | BDL*(DL**=0.0008) | BDL*(DL**=0.002) | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.019 | BDL*(DL**=0.0009) | BDL*(DL**=0.001) | 0.041 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.064 | BDL*(DL**=0.0006) |  |  |  | 1570 |  |  |  | Non-Complying | Non-Complying |  | 7.48 | 110 | 344 | 8.6 | 290 | 1310 | 191.6 | 360 | 140 | 3.29 | 24.78 | 5.68 | 11.4 |  | 2.85 | 1.6 |  | 434.116 | 49.81 | 82.16 |  |  | 480 | 420 | 7000 |  |  | 9.31 |  |  | 0.245 | BDL*(DL**=0.00016) | 2.115 | 0.315 | 0.022 | 0.047 | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.019 | BDL*(DL**=0.0009) | BDL*(DL**=0.001) | 0.041 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.064 | BDL*(DL**=0.0006) |  |  |  | 2360
86 | (PWL-STP-002) 4.5 MLD STP Hathin Palwal by PHED in 31.12.2015 |  | 30 | 7-8.5 | 100 | 40
[11 empty] | 06.01.2026 | 1905 dt. 16.01.2026 |  | 1: 7.21; 2: 75; 3: 368; 5: 170; 11: 14.01; 25: 840 |  |  |  | Non-Complying | Non-Complying
[11 empty] | 04.02.2026 | 2233 dt. 12.02.2026 |  | 1: 7.43; 2: 27; 3: 133.05; 5: 55; 11: 12.6; 25: 290 |  |  |  | Non-Complying | Non-Complying |  | 7.12 | 82 | 330.6 |  | 260 | [5 empty] | 30.82 | [13 empty] | 7000
[11 empty] | 09.03.2026 | 2565 dt. 17.02.2026 |  | 1: 7.96; 2: 72; 3: 328; 5: 125; 11: 20.02; 25: 1300 |  |  |  | Non-Complying | Non-Complying
[11 empty] | 02.04.2026 | 15 dt. 10.04.2026 (Bypass) |  | 1: 7.1; 2: 95; 3: 392; 5: 175; 11: 24.12; 25: 1500 |  |  |  | Non-Complying | Non-Complying
[11 empty] | 05.05.2026 | 230 dt.13.05.2026 |  | 1: 7.42; 2: 95; 3: 408; 5: 270; 11: 22.72; 25: 1100 |  |  |  | Non-Complying | Non-Complying |  | 7.6 | 115 | 456 |  | 310 | [5 empty] | 36.14 | [13 empty] | 4100
[11 empty] | 04.06.2026 | 408 dt. 11.06.2026 |  | 1: 7.58; 2: 13; 3: 68; 5: 17; 11: 12.6; 25: 330 |  |  |  | Non-Complying | Non-Complying |  | 7.64 | 105 | 408 |  | 340 | [5 empty] | 38.76 | [13 empty] | 7000
| 1st Phase July, 2026 | [9 empty] | 06.07.2026 | 294 M dt. 14.07.2026 | - | 1: 8.08; 2: 14; 3: 64; 5: 17; 11: 15.06; 25: 240; 52: BDL*(DL**=4); 55: 2620 |  |  |  | Non-Complying | Non-Complying | 630.18 | 7.12 | 130 | 472 |  | 270 | [5 empty] | 28.02 | [13 empty] | 8400 | [26 empty] | 9.4
| 2nd Phase July, 2026 | [9 empty] | 20.07.2026 | 361 M dt. 29.07.2026 |  | 7.78 | 9.4 | 40 | BDL*(DL**=4) | 18 | 2010 | 1399.4 | 270 | 149 | 0.55 | 14.26 | BDL*(DL**=0.5) | 4.2 |  | 1.1 | ND |  | 589.867 | 190.408 | 219.741 |  |  | 310 | 1590 | 190 |  |  | 7.03 |  |  | 0.366 | BDL*(DL**=0.0004) | 0.103 | 0.05 | BDL*(DL**=0.0002) | BDL*(DL**=0.0005) | BDL*(DL**=0.001) | BDL*(DL**=0.001) | BDL*(DL**=0.0001) | BDL*(DL**=0.0002) | 0.031 | 0.005 | BDL*(DL**=0.001) | 0.076 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.099 | BDL*(DL**=0.0006) | BDL*(DL**=4) |  |  | 3640 |  |  |  | Non-Complying | Non-Complying |  | 7.52 | 92 | 232 | 6.8 | 245 | 3040 | 1034.5 | 130 | 184 | 1.74 | 31.12 | 2.84 | 3.8 |  | 1.42 | 1.2 |  | 857.404 | 293.097 | 354.25 |  |  | 250 | 2205 | 6300 |  |  | 8.15 |  |  | 0.344 | BDL*(DL**=0.0004) | 4.753 | 0.101 | 0.016 | BDL*(DL**=0.0005) | 0.012 | BDL*(DL**=0.001) | BDL*(DL**=0.0001) | BDL*(DL**=0.0002) | 0.165 | 0.026 | BDL*(DL**=0.001) | 5.406 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.159 | BDL*(DL**=0.0006) | BDL*(DL**=4) |  |  | 5530
[11 empty] | 03.08.2026 | 407 M dt. 11.08.2026 | 1.87 | 7.02 | 7.6 | 48 |  | 18 | 1060 | 357.2 | 250 | 144 | 0.66 | 5.12 | BDL*(DL**=0.5) | 4.7 |  | 0.74 | ND |  | 353.708 | 52.974 | 86.397 |  |  | 460 | 440 | 150 |  |  | 7.39 |  |  | 0.334 | 0.005 | 0.134 | 0.066 | 0.003 | 0.001 | 0.004 | BDL*(DL**=0.001) | 0.001 | BDL*(DL**=0.0007) | 0.087 | 0.017 | BDL*(DL**=0.001) | 0.05 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.036 | BDL*(DL**=0.0006) | BDL*(DL**=4) |  |  | 1920 |  |  |  | Non-Complying | Non-Complying |  | 7.48 | 110 | 344 | 8.6 | 290 | 1310 | 191.6 | 360 | 140 | 3.29 | 24.78 | 5.68 | 11.4 |  | 2.85 | 1.6 |  | 434.116 | 49.81 | 82.16 |  |  | 480 | 420 | 7000 |  |  | 9.31 |  |  | 0.245 | BDL*(DL**=0.00016) | 2.115 | 0.315 | 0.022 | 0.047 | BDL*(DL**=0.0061) | BDL*(DL**=0.001) | BDL*(DL**=0.0004) | BDL*(DL**=0.0007) | 0.019 | BDL*(DL**=0.0009) | BDL*(DL**=0.001) | 0.041 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.064 | BDL*(DL**=0.0006) |  |  |  | 2360
87 | (PWL-STP-003) 9 MLD STP, Hodal, Palwal by PHED in May, 2013 (MBBR &TT) |  | 10 | 5.5-9 | 100 | 10
[11 empty] | 06.01.2026 | 1902 dt. 16.01.2026 | - | 1: 7.31; 2: 7.5; 3: 36; 5: 13; 11: 7; 25: 79 |  |  |  | Complying | Complying | 835.07 | 7.05 | 90 | 368 |  | 260 | [5 empty] | 39.16 | [13 empty] | 6300
[11 empty] | 06.02.2026 | 2281 dt. 14.02.2026 |  | 1: 7.31; 2: 9.5; 3: 48.3; 5: 19; 11: 9.8; 25: 93 |  |  |  | Complying | Complying |  | 7.2 | 115 | 467.7 |  | 285 | [5 empty] | 28.26 | [13 empty] | 5800
[11 empty] | 10.03.2026 | 2575 dt. 20.02.2026 |  | 1: 7.11; 2: 8.4; 3: 44; 5: 17; 11: 8.36; 25: 84 |  |  |  | Complying | Complying |  | 7.76 | 105 | 424 |  | 270 | [5 empty] | 32.34 | [13 empty] | 6300
| Apr., 2026 | [9 empty] | 08.04.2026 | 88 dt. 17.04.2026 |  | 1: 7.38; 2: 12; 3: 56; 5: 24; 11: 13.53; 25: 170 |  |  |  | Non-Complying | Non-Complying |  | 7.84 | 98 | 416 |  | 290 | [5 empty] | 42.16 | [13 empty] | 7900
| May. 2026 | [9 empty] | 05.05.2026 | 228 dt.12.05.2026 | - | 1: 7.29; 2: 24; 3: 128; 5: 48; 11: 18.04; 25: 790 |  |  |  | Non-Complying | Non-Complying | 216.21 | 7.13 | 105 | 456 |  | 255 | [5 empty] | 39.74 | [13 empty] | 8400
[11 empty] | 02.06.2026 | 397 dt. 10.06.2026 |  | 1: 8.28; 2: 16; 3: 72; 5: 29; 11: 14.01; 25: 330 |  |  |  | Non-Complying | Non-Complying |  | 7.25 | 120 | 488 |  | 305 | [5 empty] | 42.16 | [13 empty] | 7000
| 1st Phase July, 2026 | [9 empty] | 06.07.2026 | 293 M dt. 14.07.2026 | - | 1: 7.82; 2: 15; 3: 68; 5: 18; 11: 18.02; 25: 390; 52: BDL*(DL**=4); 55: 1880 |  |  |  | Non-Complying | Non-Complying | 630.18 | 7.96 | 130 | 496 |  | 320 | [5 empty] | 38.55 | [13 empty] | 9300 | [26 empty] | 7.4
| 2nd Phase July, 2026 | [9 empty] | 20.07.2026 | 360 M dt. 29.07.2026 |  | 7.49 | 15 | 68 | BDL*(DL**=4) | 31 | 2180 | 1399.4 | 500 | 107 | 0.96 | 14.48 | 2.75 | 3.7 |  | 4.92 | ND |  | 649.168 | 176.488 | 132.562 |  |  | 700 | 1070 | 930 |  |  | 8.68 |  |  | 0.459 | BDL*(DL**=0.0004) | 0.131 | 0.096 | BDL*(DL**=0.0002) | BDL*(DL**=0.0005) | BDL*(DL**=0.001) | BDL*(DL**=0.001) | BDL*(DL**=0.0001) | BDL*(DL**=0.0002) | 0.053 | 0.003 | BDL*(DL**=0.001) | 0.072 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.079 | BDL*(DL**=0.0006) | BDL*(DL**=4) |  |  | 3960 |  |  |  | Non-Complying | Non-Complying |  | 7.52 | 92 | 232 | 6.8 | 245 | 3040 | 1034.5 | 130 | 184 | 1.74 | 31.12 | 2.84 | 3.8 |  | 1.42 | 1.2 |  | 857.404 | 293.097 | 354.25 |  |  | 250 | 2205 | 6300 |  |  | 8.15 |  |  | 0.344 | BDL*(DL**=0.0004) | 4.753 | 0.101 | 0.016 | BDL*(DL**=0.0005) | 0.012 | BDL*(DL**=0.001) | BDL*(DL**=0.0001) | BDL*(DL**=0.0002) | 0.165 | 0.026 | BDL*(DL**=0.001) | 5.406 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.159 | BDL*(DL**=0.0006) | BDL*(DL**=4) |  |  | 5530
[11 empty] | 06.08.2026 | 641 M dt. 13.08.2026 | Not working | 7.24 | 14 | 72 | BDL*(DL**=4) | 25 | 2320 | 1057.1 | 480 | 150 | 0.89 | 12.48 | 1.06 | 4.2 |  | 2.37 | ND |  | 608.178 | 92.82 | 153.1 |  |  | 500 | 780 | 490 |  |  | 9.54 |  |  | 0.313 | 0.024 | 0.313 | 0.082 | 0.004 | 0.002 | 0.002 | BDL*(DL**=0.001) | 0.001 | BDL*(DL**=0.0007) | 0.144 | 0.024 | BDL*(DL**=0.001) | 0.132 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.059 | BDL*(DL**=0.0006) |  |  |  | 4210 |  |  |  | Non-Complying | Non-Complying |  | 7.54 | 125 | 424 | 11.2 | 305 | 2320 | 513.8 | 510 | 165 | 2.06 | 22.11 | 3.49 | 15.8 |  | 3.13 | 1.8 |  | 710.142 | 100.6 | 165.93 |  |  | 620 | 830 | 9300 |  |  | 10.74 |  |  | 0.528 | 0.031 | 11.295 | 0.319 | 0.007 | 0.018 | 0.106 | BDL*(DL**=0.001) | 0.004 | BDL*(DL**=0.0007) | 0.208 | 0.036 | BDL*(DL**=0.001) | 7.058 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.149 | BDL*(DL**=0.0006) |  |  |  | 4620
88 | (PWL-STP-005) 15 MLD STP, Village Jodhpur, Palwal by ULBD in 31.05.2023
[11 empty] | 05.01.2026 | 1876 dt. 14.01.2026 |  | 1: 7.24; 2: 14; 3: 68; 5: 25; 11: 12.64; 25: 330 |  |  |  | Non-Complying | Non-Complying |  | 7.53 | 80 | 328 |  | 235 | [5 empty] | 36.24 | [13 empty] | 5800
[11 empty] | 04.02.2026 | 2234 dt. 12.02.2026 |  | 1: 7.32; 2: 16; 3: 72.5; 5: 32; 11: 14.01; 25: 410 |  |  |  | Non-Complying | Non-Complying |  | 7.58 | 95 | 387.07 |  | 250 | [5 empty] | 39.12 | [13 empty] | 6300
[11 empty] | 09.03.2026 | 2563 dt. 17.03.2026 |  | 1: 7.46; 2: 24; 3: 108; 5: 52; 11: 15.61; 25: 580 |  |  |  | Non-Complying | Non-Complying |  | 8.52 | 88 | 352 |  | 275 | [5 empty] | 40.36 | [13 empty] | 7900
| Apr., 2026 | [9 empty] | 09.04.2026 | 92 dt. 21.04.2026 |  | 1: 7.41; 2: 27; 3: 120; 5: 58; 11: 14.01; 25: 630 |  |  |  | Non-Complying | Non-Complying |  | 7.13 | 125 | 448 |  | 320 | [5 empty] | 38.04 | [13 empty] | 9300
| May. 2026 | [9 empty] | 14.05.2026 | 274 dt.21.05.2026 |  | 1: 6.92; 2: 24; 3: 92; 5: 32; 11: 12.6; 25: 490 |  |  |  | Non-Complying | Non-Complying |  | 7.79 | 105 | 392 |  | 270 | [5 empty] | 39.84 | [13 empty] | 8800
[11 empty] | 03.06.2026 | 405 dt. 11.06.2026 |  | 1: 7.43; 2: 5.6; 3: 28; 5: 13; 25: 49 |  |  |  | Complying | Complying |  | 6.13 | 108 | 432 |  | 315 | [19 empty] | 6300
| 1st Phase July, 2026 | [9 empty] | 01.07.2026 | 464 dt. 09.07.2026 |  | 1: 7.16; 2: 32; 3: 124; 5: 38; 11: 14.04; 25: 330; 52: BDL*(DL**=4); 55: 1110 |  |  |  | Non-Complying | Non-Complying |  | 6.36 | 105 | 360 |  | 325 | [5 empty] | 28.02 | [13 empty] | 7000 | [26 empty] | 8.8
| 2nd Phase July, 2026 | [9 empty] | 21.07.2026 | 365 M dt. 29.07.2026 |  | 7.81 | 14 | 72 | BDL*(DL**=4) | 46 | 810 | 307.3 | 345 | 73 | 0.76 | 11.26 | BDL*(DL**=0.5) | 4.2 |  | 2.73 | ND |  | 303.172 | 55.746 | 63.133 |  |  | 455 | 570 | 150 |  |  | 6.7 |  |  | 0.206 | BDL*(DL**=0.0004) | 0.008 | 0.016 | BDL*(DL**=0.0002) | BDL*(DL**=0.0005) | BDL*(DL**=0.001) | BDL*(DL**=0.001) | BDL*(DL**=0.0001) | BDL*(DL**=0.0002) | 0.017 | 0.01 | BDL*(DL**=0.001) | 0.093 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.025 | BDL*(DL**=0.0006) | BDL*(DL**=4) |  |  | 1480 |  |  |  | Non-Complying | Non-Complying |  | 7.04 | 85 | 256 | 7.6 | 310 | 680 | 344.8 | 260 | 90 | 3.26 | 30.43 | 1.64 | 2.8 |  | 5.14 | 1.8 |  | 221.574 | 47.327 | 69.274 |  |  | 460 | 490 | 4900 |  |  | 5.02 |  |  | 0.089 | BDL*(DL**=0.0004) | 1.541 | 0.092 | 0.035 | BDL*(DL**=0.0005) | 0.018 | BDL*(DL**=0.001) | BDL*(DL**=0.0001) | BDL*(DL**=0.0002) | 0.078 | 0.129 | BDL*(DL**=0.001) | 3.318 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.26 | BDL*(DL**=0.0006) | BDL*(DL**=4) |  |  | 1240
[11 empty] | 06.08.2026 | 646 dt. 13.08.2026 | Not installed | 7.12 | 12 | 64 | BDL*(DL**=4) | 22 | 1270 | 449.8 | 435 | 123 | 0.74 | 6.48 | 1.12 | 2.1 |  | 2.35 | ND |  | 328.958 | 50.3 | 82.96 |  |  | 505 | 420 | 130 |  |  | 6.62 |  |  | 0.149 | 0.018 | 0.571 | 0.104 | 0.03 | 0.005 | 0.002 | BDL*(DL**=0.001) | 0.001 | BDL*(DL**=0.0007) | 0.071 | 0.067 | BDL*(DL**=0.001) | 0.172 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.098 | BDL*(DL**=0.0006) |  |  |  | 2320 |  |  |  | Non-Complying | Non-Complying |  | 6.96 | 102 | 304 | 10.4 | 285 | 1450 | 329.6 | 515 | 148 | 2.19 | 35.72 | 4.64 | 15.9 |  | 2.35 | 1.4 |  | 408.156 | 58.56 | 96.59 |  |  | 540 | 484 | 7000 |  |  | 8.08 |  |  | 0.246 | 0.313 | 1.295 | 0.108 | 0.043 | 0.063 | 0.024 | BDL*(DL**=0.001) | 0.003 | BDL*(DL**=0.0007) | 0.175 | 0.081 | BDL*(DL**=0.001) | 1.058 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.104 | BDL*(DL**=0.0006) |  |  |  | 2640
89 | (PWL-STP-006) 2.5 MLD STP, Ferozpur, Palwal by ULBD in 31.05.2023
[11 empty] | 05.01.2026 | 1878 dt. 14.01.2026 |  | 1: 8.14; 2: 13; 3: 64; 5: 32; 11: 12.6; 25: 490 |  |  |  | Non-Complying | Non-Complying |  | 7.49 | 85 | 344 |  | 240 | [5 empty] | 30.82 | [13 empty] | 8400
[11 empty] | 05.02.2026 | 2273 dt. 13.02.2026 |  | 1: 8.46; 2: 16; 3: 96.7; 5: 35; 11: 14.01; 25: 330 |  |  |  | Non-Complying | Non-Complying |  | 7.43 | 104 | 435.4 |  | 255 | [5 empty] | 39.66 | [13 empty] | 6300
[11 empty] | 10.03.2026 | 2562 dt. 17.03.2026 |  | 1: 7.22; 2: 14; 3: 88; 5: 38; 11: 12.8; 25: 430 |  |  |  | Non-Complying | Non-Complying |  | 7.69 | 96 | 392 |  | 235 | [5 empty] | 40.12 | [13 empty] | 8400
| Apr., 2026 | [9 empty] | 09.04.2026 | 90 dt. 21.04.2026 |  | 1: 8.73; 2: 12; 3: 68; 5: 35; 11: 11.6; 25: 390 |  |  |  | Non-Complying | Non-Complying |  | 7.45 | 135 | 480 |  | 255 | [5 empty] | 48.44 | [13 empty] | 9300
| May. 2026 | [9 empty] | 07.05.2026 | 237 dt.14.05.2026 |  | 1: 7.88; 2: 14; 3: 72; 5: 27; 11: 14.01; 25: 700 |  |  |  | Non-Complying | Non-Complying |  | 6.65 | 120 | 424 |  | 340 | [5 empty] | 46.68 | [13 empty] | 11000
[11 empty] | 05.06.2026 | 410 dt. 11.06.2026 |  | 1: 7.48; 2: 12; 3: 64; 5: 34; 11: 16.64; 25: 580 |  |  |  | Non-Complying | Non-Complying |  | 7.56 | 102 | 392 |  | 255 | [5 empty] | 42.53 | [13 empty] | 8400
| 1st Phase July, 2026 | [9 empty] | 01.07.2026 | 466 dt. 09.07.2026 |  | 1: 8.39; 2: 20; 3: 60; 5: 40; 11: 12.92; 25: 490; 52: BDL*(DL**=4); 55: 1580 |  |  |  | Non-Complying | Non-Complying |  | 7.58 | 135 | 440 |  | 290 | [5 empty] | 38.26 | [13 empty] | 9300 | [26 empty] | 7.2
| 2nd Phase July, 2026 | [9 empty] | 21.07.2026 | 367 M dt. 29.07.2026 |  | 7.79 | 22 | 96 |  | 52 | 1090 | 499.8 | 370 | 104 | 0.95 | 13.92 | BDL*(DL**=0.5) | 7.5 |  | 1.68 | ND |  | 571.235 | 45.796 | 31.58 |  |  | 500 | 375 | 210 |  |  | 15.19 |  |  | 0.478 | BDL*(DL**=0.0004) | 0.062 | 0.09 | BDL*(DL**=0.0002) | BDL*(DL**=0.0005) | BDL*(DL**=0.001) | BDL*(DL**=0.001) | BDL*(DL**=0.0001) | BDL*(DL**=0.0002) | 0.015 | 0.006 | BDL*(DL**=0.001) | 0.099 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.043 | BDL*(DL**=0.0006) | BDL*(DL**=4) |  |  | 1990 |  |  |  | Non-Complying | Non-Complying |  | 7.09 | 160 | 520 |  | 265 | 1190 | 709.7 | 1020 | 185 | 4.76 | 38.42 | BDL*(DL**=0.5) | 4.6 |  | 4.8 | 2.6 |  | 556.907 | 60.501 | 107.317 |  |  | 1180 | 560 | 5800 |  |  | 10.65 |  |  | 0.526 | BDL*(DL**=0.0004) | 10.027 | 0.758 | 0.048 | 0.032 | 0.012 | BDL*(DL**=0.001) | BDL*(DL**=0.0001) | BDL*(DL**=0.0002) | 0.084 | 0.114 | BDL*(DL**=0.001) | 8.622 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.258 | BDL*(DL**=0.0006) | BDL*(DL**=4) |  |  | 2180
[11 empty] | 06.08.2026 | 647 dt. 13.08.2026 | Not installed | 8.06 | 17 | 76 |  | 28 | 1630 | 529.8 | 295 | 109 | 0.35 | 9.84 | 0.82 | 2.3 |  | 0.86 | ND |  | 701.882 | 0.091 | 91.38 |  |  | 425 | 464 | 270 |  |  | 14.29 |  |  | 0.39 | 0.025 | 0.34 | 0.091 | 0.002 | 0.005 | 0.004 | BDL*(DL**=0.001) | 0.001 | BDL*(DL**=0.0007) | 0.069 | 0.061 | BDL*(DL**=0.001) | 0.467 |  |  | 0.003 | BDL*(DL**=0.002) |  | 0.038 | BDL*(DL**=0.0006) | BDL*(DL**=4) |  |  | 2960 |  |  |  | Non-Complying | Non-Complying |  | 7.99 | 145 | 488 |  | 320 | 1680 | 424.6 | 480 | 120 | 2.96 | 44.26 | 6.38 | 11.8 |  | 3.19 | 1.2 |  | 723.058 | 59.53 | 98.19 |  |  | 510 | 492 | 11000 |  |  | 14.19 |  |  | 0.644 | 0.051 | 6.145 | 0.106 | 0.008 | 0.008 | 0.009 | BDL*(DL**=0.001) | 0.003 | BDL*(DL**=0.0007) | 0.725 | 0.074 | BDL*(DL**=0.001) | 3.155 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.185 | BDL*(DL**=0.0006) | 7.2 |  |  | 3040
90 | (PWL-STP-007) 10 MLD STP, Kithwari/ Agwanpur, Palwal by ULBD in 31.08.2023
[11 empty] | 05.01.2026 | 1877 dt. 14.01.2026 |  | 1: 7.67; 2: 24; 3: 108; 5: 62; 11: 18.21; 25: 770 |  |  |  | Non-Complying | Non-Complying | 227.3 | 7.13 | 120 | 484 |  | 240 | [5 empty] | 42.18 | [13 empty] | 9300
[11 empty] | 05.02.2026 | 2274 dt. 13.02.2026 |  | 1: 7.43; 2: 25; 3: 116.9; 5: 42; 11: 15.6; 25: 630 |  |  |  | Non-Complying | Non-Complying |  | 7.6 | 90 | 370.9 |  | 210 | [5 empty] | 34.28 | [13 empty] | 5800
[11 empty] | 09.03.2026 | 2564 dt. 17.02.2026 |  | 1: 7.91; 2: 44; 3: 208; 5: 82; 11: 18.2; 25: 930 |  |  |  | Non-Complying | Non-Complying |  | 7.68 | 105 | 424 |  | 275 | [5 empty] | 39.96 | [13 empty] | 8400
[11 empty] | 09.04.2026 | 91 dt. 21.04.2026 |  | 1: 7.31; 2: 40; 3: 168; 5: 65; 11: 20.01; 25: 790 |  |  |  | Non-Complying | Non-Complying |  | 7.92 | 112 | 392 |  | 240 | [5 empty] | 45.18 | [13 empty] | 11000
[11 empty] | 07.05.2026 | 238 dt.14.05.2026 |  | 1: 7.17; 2: 35; 3: 144; 5: 82; 11: 28.02; 25: 930 |  |  |  | Non-Complying | Non-Complying |  | 7.25 | 120 | 472 |  | 275 | [5 empty] | 49.12 | [13 empty] | 8400
[11 empty] | 05.06.2026 | 409 dt. 11.06.2026 |  | 1: 7.76; 2: 19; 3: 96; 5: 37; 11: 20.24; 25: 1100 |  |  |  | Non-Complying | Non-Complying |  | 8.13 | 115 | 448 |  | 290 | [5 empty] | 46.41 | [13 empty] | 9300
| 1st Phase July, 2026 | [9 empty] | 01.07.2026 | 465 dt. 09.07.2026 |  | 1: 7.4; 2: 24; 3: 84; 5: 44; 11: 16.72; 25: 930; 52: BDL*(DL**=4); 55: 1370 |  |  |  | Non-Complying | Non-Complying |  | 8.24 | 120 | 392 |  | 305 | [5 empty] | 32.84 | [13 empty] | 8400 | [26 empty] | 8.2
| 2nd Phase July, 2026 | [9 empty] | 21.07.2026 | 366 M dt. 29.07.2026 |  | 7.51 | 12 | 68 | BDL*(DL**=4) | 42 | 1070 | 519.7 | 360 | 130 | 0.42 | 12.48 | BDL*(DL**=0.5) | 5.4 |  | 1.43 | ND |  | 171.515 | 29.408 | 39.88 |  |  | 530 | 645 | 1500 |  |  | 5.02 |  |  | 0.262 | BDL*(DL**=0.0004) | 0.024 | 0.014 | BDL*(DL**=0.0002) | BDL*(DL**=0.0005) | BDL*(DL**=0.001) | BDL*(DL**=0.001) | BDL*(DL**=0.0001) | BDL*(DL**=0.0002) | BDL*(DL**=0.0003) | 0.005 | BDL*(DL**=0.001) | 0.034 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.04 | BDL*(DL**=0.0006) |  |  |  | 1960 |  |  |  | Non-Complying | Non-Complying |  | 7.13 | 104 | 320 |  | 275 | 1090 | 564.7 | 480 | 118 | 2.53 | 26.28 | 2.72 | 2.9 |  | 4.02 | 1.8 |  | 397.629 | 77.883 | 105.523 |  |  | 700 | 660 | 7900 |  |  | 7.16 |  |  | 0.208 | BDL*(DL**=0.0004) | 3.04 | 0.122 | 0.024 | 0.017 | BDL*(DL**=0.001) | BDL*(DL**=0.001) | BDL*(DL**=0.0001) | BDL*(DL**=0.0002) | 0.097 | 0.106 | BDL*(DL**=0.001) | 3.581 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.199 | BDL*(DL**=0.0006) |  |  |  | 1990
[11 empty] | 06.08.2026 | 645 dt. 13.08.2026 | Not installed | 7.31 | 16 | 80 | BDL*(DL**=4) | 29 | 880 | 254.9 | 280 | 77 | 0.55 | 14.01 | BDL*(DL**=0.5) | 6.8 |  | 1.72 | ND |  | 205.312 | 34.99 | 57.71 |  |  | 290 | 340 | 790 |  |  | 5.26 |  |  | 0.056 | 0.003 | 0.245 | 0.103 | 0.002 | 0.004 | 0.001 | BDL*(DL**=0.001) | 0.001 | BDL*(DL**=0.0007) | 0.041 | 0.023 | BDL*(DL**=0.001) | 0.133 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.077 | BDL*(DL**=0.0006) |  |  |  | 1610 |  |  |  | Non-Complying | Non-Complying |  | 7.25 | 115 | 352 | 8.2 | 290 | 730 | 210.8 | 290 | 145 | 3.04 | 30.26 | 7.82 | 12.2 |  | 3.69 | 2.8 |  | 190.416 | 29.4 | 48.4 |  |  | 320 | 245 | 5800 |  |  | 5.32 |  |  | 0.104 | 0.006 | 0.312 | 0.209 | 0.007 | 0.009 | 0.007 | BDL*(DL**=0.001) | 0.007 | BDL*(DL**=0.0007) | 0.0075 | 0.915 | BDL*(DL**=0.001) | 2.116 |  |  | BDL*(DL**=0.0005) | BDL*(DL**=0.002) |  | 0.206 | BDL*(DL**=0.0006) |  |  |  | 1320
Kurukshetra
91 | (KUK-STP-001) 7 MLD STP Ladwa Kurukshetra by PHED in 31.10.2016 |  | 10 | 6.5 to 9 | 50 | 20
[11 empty] | 09.01.2026 | 4261 dt. 21.01.2026 |  | 1: 7.48; 2: 7.8; 3: 44; 5: 15; 11: ND |  |  |  | Complying | Complying |  | 7.19 | 140 | 492 |  | 288 | [5 empty] | 15.84
[11 empty] | 10.02.2026 | 4463 dt. 23.02.2026 | 6.2 | 1: 7.77; 2: 7; 3: 36; 5: 14; 11: ND |  |  |  | Complying | Complying | - | 7.05 | 120 | 392 |  | 155 | [5 empty] | 14.65 | [13 empty] | -
[11 empty] | 06.03.2026 | 4649 dt. 19.03.2026 | 4.25 | 1: 826; 2: 5.8; 3: 36; 5: 10; 11: 5.32 |  |  |  | Complying | Complying | 4.4 | 7.44 | 170 | 580 |  | 122 | [5 empty] | 16.98 | [13 empty] | -
[11 empty] | 02.04.2026 | 38 dt. 17.04.2026 | 166.94 | 1: 7.86; 2: 8; 3: 44; 5: 16; 11: ND |  |  |  | Complying | Complying | - | 7.19 | 140 | 500 |  | 264 | [5 empty] | 14.73 | [13 empty] | -
[11 empty] | 08.05.2026 | 221 dt. 18.05.2026 |  | 1: 7.92; 2: 7.8; 3: 48; 5: 17; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 7.8 | 135 | 440 |  | 256 | [5 empty] | 19.72 | [13 empty] | -
[11 empty] | 02.06.2026 | 418 dt. 15.06.2026 | 154.38 | 1: 7.69; 2: 5.5; 3: 32; 5: 9; 11: 8.02; 25: 90 |  |  |  | Complying | Complying |  | 7.35 | 94 | 312 |  | 116 | [5 empty] | 18.76 | [13 empty] | 1.82X105
[11 empty] | 02.07.2026 | 573 dt. 10.07.2026 | 152.37 | 1: 7.56; 2: 4.8; 3: 20; 5: 7; 11: 1.08; 25: 70; 52: BDL |  |  |  | Complying | Complying | - | 6.96 | 135 | 444 |  | 295 | [5 empty] | 22.24 | [13 empty] | 1.22X105 | [26 empty] | 26
Ghaggar Catchment
Ambala
1 | (AMB-STP-001) 3.00 MLD STP Naya Gaon , Unit.II , Ambala City by PHED in Janurary, 2011 |  | 20 | 7 to 8.50 | 100 | 30
[11 empty] | 09.01.2026 | 4266 dt. 21.01.2026 |  | 1: 7.26; 2: 6.5; 3: 44; 5: 11; 11: ND |  |  |  | Complying | Complying
|  | 2026-02-16 | 4525, 02.03.2026 | [7 empty] | 16.02.2026 | 4525, 02.03.2026 | 238.77 | 1: 7.87; 2: 7.6; 3: 48; 5: 14; 11: ND; 25: 90 |  |  |  | Complying | Complying
|  | 2026-03-12 | 4703, 25.03.2026 | [7 empty] | 12.03.2026 | 4703, 25.03.2026 | _ | 1: 8.19; 2: 6.4; 3: 36; 5: 11; 11: ND; 25: 70 |  |  |  | Complying | Complying
|  | 2026-04-09 | 108, 28.04.2026 | [7 empty] | 09.04.2026 | 108, 28.04.2026 | 105.3 | 1: 7.86; 2: 6.5; 3: 36; 5: 11; 11: ND; 25: 60 |  |  |  | Complying | Complying
|  | 2026-05-20 | 292, 01.06.2026 | [7 empty] | 20.05.2026 | 292, 01.06.2026 | 369.93 | 1: 8.24; 2: 5.5; 3: 28; 5: 9; 11: 7.82; 25: 80 |  |  |  | Complying | Complying
|  | 2026-06-03 | 406, 15.06.2026 | [7 empty] | 03.06.2026 | 406, 15.06.2026 | 16.18 | 1: 8.56; 2: 7.2; 3: 40; 5: 3; 11: 18.41; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 03.07.2026 | 592 dt. 13.07.2026 |  | 1: 7.86; 2: 7.6; 3: 40; 5: 11; 11: 7.92; 15: 0.98; 25: 80; 52: BDL(DL=02); 55: 869 |  |  |  | Complying | Complying
2 | (AMB-STP-002) 3.25 MLD STP Naya Gaon, Unit.I Ambala City by PHED in 1.4.2016 |  | 20 | 7 to 8.50 | 100 | 40
[11 empty] | 09.01.2026 | 4266 dt. 21.01.2026 |  | 1: 7.26; 2: 6.5; 3: 44; 5: 11; 11: ND |  |  |  | Complying | Complying
[11 empty] | 16.02.2026 | 4525, 02.03.2026 |  | 1: 7.87; 2: 7.6; 3: 48; 5: 14; 11: ND; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 12.03.2026 | 4703, 25.03.2026 |  | 1: 8.19; 2: 6.4; 3: 36; 5: 11; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 09.04.2026 | 108, 28.04.2026 |  | 1: 7.86; 2: 6.5; 3: 36; 5: 11; 11: ND; 25: 60 |  |  |  | Complying | Complying
[11 empty] | 20.05.2026 | 292, 01.06.2026 |  | 1: 8.24; 2: 5.5; 3: 28; 5: 9; 11: 7.82; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 03.06.2026 | 406, 15.06.2026 |  | 1: 8.56; 2: 7.2; 3: 40; 5: 3; 11: 18.41; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 03.07.2026 | 592 dt. 13.07.2026 |  | 1: 7.86; 2: 7.6; 3: 40; 5: 11; 11: 7.92; 15: 0.98; 25: 80; 52: BDL(DL=02); 55: 869 |  |  |  | Complying | Complying
3 | (AMB-STP-003) 2 MLD STP Sec.7 , Urban Estate , Ambala City Ambala by HUDA in 10.9.2015 | HSVP | 10 | 7-8.5 | 100 | 10 |  |  |  | 1000
[11 empty] | 14.01.2026 | 4321 dt. 29.01.2026 | 29.3 | 1: 8.5; 2: 6.5; 3: 44; 5: 9; 11: ND |  |  |  | Complying | Complying
[11 empty] | 11.02.2026 | 4499 dt. 24.02.2026 | 31 | 1: 8.06; 2: 6.2; 3: 36; 5: 8; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 09.03.2026 | 4665 dt. 19.03.2026 | 175789.469 | 1: 7.43; 2: 5.8; 3: 36; 5: 6; 11: 2.87; 25: ND |  |  |  | Complying | Complying
[11 empty] | 06.04.2026 | 42 dt. 22.04.2026 | 68.7 | 1: 7.63; 2: 5.2; 3: 24; 5: 6; 11: ND; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 04.05.2026 | 176 dt. 12.05.2026 | 11.7 | 1: 7.19; 2: 5.6; 3: 36; 5: 11; 11: ND; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 03.06.2026 | 409 dt. 15.06.2026 | 189582.115 | 1: 7.77; 2: 7.4; 3: 44; 5: 18; 11: 9.734; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 02.07.2026 | 563 dt. 09.07.2026 |  | 1: 7.6; 2: 6.4; 3: 36; 5: 7; 11: 8.21; 15: 0.53; 25: 70; 52: BDL(DL=02); 55: 862 |  |  |  | Complying | Complying
4 | (AMB-STP-004) 5 MLD Baldev Nagar , Unit.I , Ambala City by PHED 1.12.2012 |  | 20 | 7 to 8.50 | 100 | 40
[11 empty] | 29.01.2026 | 4389 dt. 09.02.2026 |  | 1: 7.36; 2: 8.6; 3: 48; 5: 17; 11: 2.84 |  |  |  | Complying | Complying
[11 empty] | 24.02.2026 | 4572, 10.03.2026 | _ | 1: 7.70; 2: 8.5; 3: 48; 5: 16; 11: ND; 25: _ |  |  |  | Complying | Complying
[11 empty] | 17.03.2026 | 4720, 01.04.2026 | _ | 1: 8.25; 2: 34; 3: 172; 5: 48; 11: 23.76; 25: 600 |  |  |  | Non-Complying | Non-Complying
[11 empty] | 16.04.2026 | 146, 29.04.2026 | 8.4 | 1: 8.15; 2: 5; 3: 28; 5: 8; 11: ND; 25: ND |  |  |  | Complying | Complying
[11 empty] | 13.05.2026 | 246, 20.05.2026 | _ | 1: 8.10; 2: 12; 3: 48; 5: 14; 11: ND; 25: ND |  |  |  | Non-Complying | Non-Complying
[11 empty] | 6.06.2026 | 436 dt. 16.06.2026 |  | 1: 8.06; 2: 9.6; 3: 48; 5: 17; 11: 8.96; 25: 90; 52: 4.5 |  |  |  | Complying | Complying
[11 empty] | 03.07.2026 | 588 dt. 13.07.2026 |  | 1: 7.6; 2: 8.6; 3: 48; 5: 25; 11: 4.93; 15: 0.92; 25: 90; 52: BDL(DL=02); 55: 1400 |  |  |  | Non-Complying | Non-Complying
5 | (AMB-STP-005) 3.25 Baldev Nagar, Unit.II ,Ambala City by PHED in 1.4.2016 |  | 20 | 7 to 8.50 | 100 | 40
[11 empty] | 29.01.2026 | 4389 dt. 09.02.2026 |  | 1: 7.36; 2: 8.6; 3: 48; 5: 17; 11: 2.84 |  |  |  | Complying | Complying
[11 empty] | 24.02.2026 | 4572, 10.03.2026 | _ | 1: 7.70; 2: 8.5; 3: 48; 5: 16; 11: ND; 25: _ |  |  |  | Complying | Complying
[11 empty] | 17.03.2026 | 4720, 01.04.2026 | _ | 1: 8.25; 2: 34; 3: 172; 5: 48; 11: 23.76; 25: 600 |  |  |  | Non-Complying | Non-Complying
[11 empty] | 16.04.2026 | 146, 29.04.2026 | 8.4 | 1: 8.15; 2: 5; 3: 28; 5: 8; 11: ND; 25: ND |  |  |  | Complying | Complying
[11 empty] | 13.05.2026 | 146, 29.04.2026 | _ | 1: 8.10; 2: 12; 3: 48; 5: 14; 11: ND; 25: ND |  |  |  | Non-Complying | Non-Complying
[11 empty] | 6.06.2026 | 436 dt. 16.06.2026 |  | 1: 8.06; 2: 9.6; 3: 48; 5: 17; 11: 8.96; 25: 90; 52: 4.5 |  |  |  | Complying | Complying
[11 empty] | 03.07.2026 | 588 dt. 13.07.2026 |  | 1: 7.6; 2: 8.6; 3: 48; 5: 25; 11: 4.93; 15: 0.92; 25: 90; 52: BDL(DL=02); 55: 1400 |  |  |  | Non-Complying | Non-Complying
6 | (AMB-STP-006) 5 MLD Moti Nagar, Unit.I , Ambala City by PHED in June 2010
[11 empty] | 09.01.2026 | 4267 dt. 21.01.2026 |  | 1: 7.89; 2: 6.4; 3: 40; 5: 9; 11: ND |  |  |  | Complying | Complying
[11 empty] | 16.02.2026 | 4524, 02.03.2026 | _ | 1: 8.10; 2: 7.8; 3: 44; 5: 15; 11: 2.56; 25: 60 |  |  |  | Complying | Complying
[11 empty] | 12.03.2026 | 4704, 25.03.2026 | _ | 1: 8.23; 2: 7.2; 3: 40; 5: 9; 11: 2.72; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 09.04.2026 | 107, 28.04.2026 | 220.9 | 1: 7.76; 2: 5.8; 3: 40; 5: 10; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 06.05.2026 | 189, 12.05.2026 | 486 | 1: 7.36; 2: 7.8; 3: 36; 5: 14; 11: 2.08; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 03.06.2026 | 408, 15.06.2026 | _ | 1: 8.32; 2: 6.8; 3: 36; 5: 7; 11: 7.893; 25: ND |  |  |  | Complying | Complying
[11 empty] | 02.07.2026 | 561 dt. 09.07.2026 |  | 1: 7.57; 2: 7.6; 3: 40; 5: 11; 11: 6.97; 15: BDL(DL=0.4); 25: 50; 52: BDL(DL=02); 55: 580 |  |  |  | Complying | Complying
7 | (AMB-STP-007) 5 MLD STP Moti Nagar , Unit.II , Ambala City by PHED Ambala in 1.8.2016 |  | 20 | 7 to 8.50 | 100 | 30
[11 empty] | 09.01.2026 | 4267 dt. 21.01.2026 |  | 1: 7.89; 2: 6.4; 3: 40; 5: 9; 11: ND |  |  |  | Complying | Complying
[11 empty] | 16.02.2026 | 4524, 02.03.2026 | _ | 1: 8.10; 2: 7.8; 3: 44; 5: 15; 11: 2.56; 25: 60 |  |  |  | Complying | Complying
[11 empty] | 12.03.2026 | 4704, 25.03.2026 | _ | 1: 8.23; 2: 7.2; 3: 40; 5: 9; 11: 2.72; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 09.04.2026 | 107, 28.04.2026 | 220.9 | 1: 7.76; 2: 5.8; 3: 40; 5: 10; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 06.05.2026 | 189, 12.05.2026 | 486 | 1: 7.36; 2: 7.8; 3: 36; 5: 14; 11: 2.08; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 03.06.2026 | 408, 15.06.2026 | _ | 1: 8.32; 2: 6.8; 3: 36; 5: 7; 11: 7.893; 25: ND |  |  |  | Complying | Complying
[11 empty] | 02.07.2026 | 561 dt. 09.07.2026 |  | 1: 7.57; 2: 7.6; 3: 40; 5: 11; 11: 6.97; 15: BDL(DL=0.4); 25: 50; 52: BDL(DL=02); 55: 580 |  |  |  | Complying | Complying
8 | (AMB-STP-008) 6 MLD STP Modal Town, Ambala City by PHED in 1.7.2012 |  | 20 | 7 to 8 | 100 | 40
[11 empty] | 09.01.2026 | 4269 dt. 21.01.2026 | 169 | 1: 7; 2: 6.8; 3: 48; 5: 17; 11: ND |  |  |  | Complying | Complying
[11 empty] | 11.02.2026 | 4497, 24.02.2026 | 180 | 1: 7.74; 2: 7.2; 3: 48; 5: 11; 11: ND; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 09.03.2026 | 4666, 19.03.2026 | 191 | 1: 7.74; 2: 6; 3: 40; 5: 6.5; 11: 4.74; 25: ND |  |  |  | Complying | Complying
[11 empty] | 06.04.2026 | 43, 22.04.2026 | 183 | 1: 7.79; 2: 6.2; 3: 32; 5: 11; 11: ND; 25: 60 |  |  |  | Complying | Complying
[11 empty] | 06.05.2026 | 190, 12-05-2026 | 191 | 1: 7.49; 2: 7; 3: 28; 5: 11; 11: 1.78; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 02.06.2026 | 403, 15.06.2026 | 3521402.68 | 1: 8.06; 2: 9; 3: 36; 5: 18; 11: 5.604; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 02.07.2026 | 562 dt. 09.07.2026 |  | 1: 7.91; 2: 5.8; 3: 32; 5: 13; 11: 5.683; 15: BDL(DL=0.4); 25: 50; 52: BDL(DL=02); 55: 772 |  |  |  | Complying | Complying
9 | (AMB-STP-009) 3.25 Nasirpur Ambala City by PHED in 31.9.2016 |  | 20 | 7 to 8.50 | 100 | 30
[11 empty] | 09.01.2026 | 4268 dt. 21.01.2026 | 356.86 | 1: 7.19; 2: 5.6; 3: 44; 5: 15; 11: ND |  |  |  | Complying | Complying
[11 empty] | 10.02.2026 | 4496, 24.02.2026 | 324.18 | 1: 7.42; 2: 5; 3: 28; 5: 9; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 09.03.2026 | 4667, 19.03.2026 | 389.4 | 1: 7.26; 2: 5; 3: 36; 5: 9; 11: 1.53; 25: ND |  |  |  | Complying | Complying
[11 empty] | 09.04.2026 | 113, 28.04.2026 | 168.95 | 1: 8.49; 2: 6.5; 3: 32; 5: 9; 11: ND; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 06.05.2026 | 192, 12.05.2026 | _ | 1: 7.47; 2: 6.8; 3: 32; 5: 12; 11: 2.76; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 03.06.2026 | 407, 15.06.2026 | 1670 | 1: 8.03; 2: 8.2; 3: 44; 5: 6; 11: 19.61; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 02.07.2026 | 559 dt. 09.07.2026 |  | 1: 7.73; 2: 6.8; 3: 36; 5: 8; 11: 8.71; 15: BDL(DL=0.4); 25: 50; 52: BDL(DL=02); 55: 1568 |  |  |  | Complying | Complying
10 | (AMB-STP-010) 0.25 MLD Sadopur , Ambala PHED in 31.12.2016 |  | 10 | 7 to 8.50 | 100 | 50
[11 empty] | 05.01.2026 | 4182 dt. 15.01.2026 |  | 1: 7.23; 2: 6.5; 3: 48; 5: 15; 11: ND |  |  |  | Complying | Complying
[11 empty] | 10.02.2026 | 4495, 24.02.2026 | _ | 1: 8.46; 2: 6.4; 3: 36; 5: 9; 11: ND; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 17.03.2026 | 4723, 01.04.2026 | _ | 1: 8.63; 2: 7.2; 3: 40; 5: 14; 11: ND; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 17.04.2026 | 147, 29.04.2026 | 15.39 | 1: 8.23; 2: 7.2; 3: 48; 5: 15; 11: ND; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 07.05.2026 | 215, 14.05.2026 | 4.06 | 1: 8.76; 2: 6.8; 3: 44; 5: 13; 11: 1.048; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 04.06.2026 | 426, 15.06.2026 | 586.463 | 1: 8.76; 2: 9.2; 3: 48; 5: 13; 11: 7.982; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 03.07.2026 | 589 dt. 13.07.2026 | 17.3 | 1: 8.2; 2: 7.8; 3: 36; 5: 8; 11: 3.82; 15: BDL(DL=0.4); 25: 80; 52: BDL(DL=02); 55: 1420 |  |  |  | Non-Complying | Non-Complying
11 | (AMB-STP-011) 3.25 MLD Devi Nagar , Ambala City by PHED on 31.5.2013 |  | 20 | 7 to 8.50 | 100 | 40
[11 empty] | 05.01.2026 | 4183 dt. 15.01.2026 |  | 1: 6.98; 2: 13; 3: 72; 5: 25; 11: 8.98 |  |  |  | Non-Complying | Non-Complying
[11 empty] | 10.02.2026 | 4494, 24.02.2026 | _ | 1: 7.9; 2: 13; 3: 64; 5: 26; 11: 9.76; 25: 500 |  |  |  | Non-Complying | Non-Complying
[11 empty] | 03.03.2026 | 4630, 18.03.2026 | _ | 1: 7.9; 2: 18; 3: 84; 5: 34; 11: 7.68; 25: 400 |  |  |  | Non-Complying | Non-Complying
[11 empty] | 09.04.2026 | 109, 28.04.2026 | _ | 1: 7.91; 2: 14; 3: 68; 5: 28; 11: 9.46; 25: 800 |  |  |  | Non-Complying | Non-Complying
[11 empty] | 19.05.2026 | 291, 01.06.2026 | _ | 1: 7.94; 2: 13; 3: 68; 5: 25; 11: N.D; 25: 400 |  |  |  | Non-Complying | Non-Complying
[11 empty] | 12.06.2026 | 494 dt. 24.06.2026 |  | 1: 6.27; 2: 14; 3: 68; 5: 27; 11: 21.01; 25: 200; 52: 9.5 |  |  |  | Non-Complying | Non-Complying
[11 empty] | 03.07.2026 | 590 dt. 13.07.2026 | 32.91 | 1: 7.36; 2: 11; 3: 60; 5: 23; 11: 6.72; 15: 0.85; 25: 200; 52: BDL(DL=02); 55: 1516 |  |  |  | Non-Complying | Non-Complying
12 | (AMB-STP-012) 3 MLD STP Naraingarh, Ambala by PHED in 1.7.2014 |  | 30 | 7 to 8.50 | 100 | 50 | [78 empty] | 11.86 |  |  | 0.44
[11 empty] | 09.01.2026 | 4265 dt. 21.01.2026 | 89.43 | 1: 7.38; 2: 5.8; 3: 32; 5: 10; 11: ND |  |  |  | Complying | Complying
[11 empty] | 23.02.2026 | 4571, 10.03.2026 | 85.34 | 1: 7.63; 2: 7.2; 3: 40; 5: 10; 11: ND; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 17.03.2026 | 4721, 01.04.2026 | 87.17 | 1: 7.84; 2: 7.6; 3: 40; 5: 13; 11: 2.73; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 17.04.2026 | 150, 29.04.2026 | 85.62 | 1: 7.96; 2: 4.5; 3: 28; 5: 9; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 25.05.2026 | 336, 01.06.2026 | _ | 1: 7.92; 2: 5.8; 3: 36; 5: 11; 11: 2.08; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 07.06.2026 | 457 dt. 16.06.2026 |  | 1: 7.95; 2: 8.2; 3: 44; 5: 13; 11: 8.318; 25: 90; 52: 4.5 |  |  |  | Complying | Complying |  | 7.18 | 156 | 476 |  | 283 | [5 empty] | 317.46 | [13 empty] | 2.4X105 | [26 empty] | 36.5
13 | (AMB-STP-014) 5 MLD STP, Sector-21, Ambala by HSVP in 31.03.2021
[11 empty] | 14.01.2026 | 4320 dt. 29.01.2026 |  | 1: 7.54; 2: 5.6; 3: 40; 5: 8; 11: ND |  |  |  | Complying | Complying
[11 empty] | 11.02.2026 | 4498, 24.02.2026 | 230.28 | 1: 8.05; 2: 7; 3: 44; 5: 12; 11: ND; 25: 60 |  |  |  | Complying | Complying
[11 empty] | 09.03.2026 | 4664, 19.03.2026 | 87.826 | 1: 7.27; 2: 6.6; 3: 44; 5: 8.5; 11: 3.76; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 06.04.2026 | 44, 22.04.2026 | 47.113 | 1: 7.16; 2: 5; 3: 28; 5: 9; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 06.05.2026 | 191, 12.05.2026 | 143.7 | 1: 7.06; 2: 7.2; 3: 40; 5: 13; 11: 2.28; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 02.06.2026 | 404, 15.06.2026 | 8219544 | 1: 8.4; 2: 8.2; 3: 40; 5: 7; 11: 39.22; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 02.07.2026 | 559 dt. 09.07.2026 |  | 1: 7.17; 2: 8.2; 3: 44; 5: 10; 11: 9.76; 15: 0.71; 25: 90; 52: BDL(DL=02); 55: 882 |  |  |  | Complying | Complying
14 | (AMB-STP-015) 10 MLD STP, Babyal, Ambala by ULBD in 31.03.2023
[11 empty] | 14.01.2026 | 4322 dt. 29.01.2026 |  | 1: 8.27; 2: 5.8; 3: 36; 5: 11; 11: ND |  |  |  | Complying | Complying
[11 empty] | 14.02.2026 | 4523, 02.03.2026 |  | 1: 7.53; 2: 5.6; 3: 36; 5: 8; 11: 1.72; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 17.03.2026 | 4722, 01.04.2026 |  | 1: 7.29; 2: 6; 3: 32; 5: 8; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 09.04.2026 | 111, 28.04.2026 |  | 1: 7.97; 2: 5.8; 3: 36; 5: 11; 11: ND; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 06.05.2026 | 187, 12.05.2026 |  | 1: 7.48; 2: 6.5; 3: 32; 5: 9; 11: ND; 25: 60 |  |  |  | Complying | Complying
[11 empty] | 04.06.2026 | 427, 15.06.2026 |  | 1: 7.65; 2: 6.4; 3: 36; 5: 9; 11: 6.342; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 03.07.2026 | 592 dt. 13.07.2026 |  | 1: 7.83; 2: 6.6; 3: 32; 5: 9; 11: 5.24; 15: BDL(DL=0.4); 25: 90; 52: BDL(DL=02); 55: 889 |  |  |  | Complying | Complying
15 | 10 MLD STP,Shahpur Machhonda, Ambala Sadar, ULBD, 31.07.2025
[11 empty] | 06.01.2026 | 4216 dt. 15.01.2026 |  | 1: 7.4; 2: 5; 3: 28; 5: 7; 11: ND |  |  |  | Complying | Complying
[11 empty] | 20.02.2026 | 4561, 03.03.2026 | 1988.5 | 1: 7.3; 2: 7.6; 3: 44; 5: 13; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 12.03.2026 | 4705, 25.03.2026 | 5736.5 | 1: 7.7; 2: 5.8; 3: 32; 5: 13; 11: ND; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 09.04.2026 | 110, 28.04.2026 | 8640 | 1: 7.6; 2: 6.4; 3: 40; 5: 14; 11: ND; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 06.05.2026 | 188, 12.05.2026 | _ | 1: 7.93; 2: 7.2; 3: 40; 5: 11; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 04.06.2026 | 428, 15.06.2026 | 184064 | 1: 7.85; 2: 6; 3: 32; 5: 11; 11: 5.423; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 03.07.2026 | 591 dt. 13.07.2026 | 227085.67 | 1: 7.9; 2: 6.5; 3: 44; 5: 15; 11: 4.22; 15: BDL(DL=0.4); 25: 80; 52: BDL(DL=02); 55: 1086 |  |  |  | Complying | Complying
Kurukshetra
16 | (KUK-STP-002) 25 MLD STP Thanesar, Kurukshetra by PHED in 31.03.2020 |  | 10 | 5.5 to 9 | 50 | 10
[11 empty] | 09.01.2026 | 4260 dt. 21.01.2026 |  | 1: 8.42; 2: 7.2; 3: 32; 5: 12; 11: ND |  |  |  | Complying | Complying |  | 7.46 | 120 | 388 |  | 276 | [5 empty] | 14.82
[11 empty] | 06.02.2026 | 4442 dt. 16.02.2026 |  | 1: 7.28; 2: 7.4; 3: 44; 5: 9; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 6.99 | 110 | 388 |  | 204 | [5 empty] | 17.23
[11 empty] | 06.03.2026 | 4651 dt. 19.03.2026 |  | 1: 8.69; 2: 7.2; 3: 48; 5: 9; 11: ND; 25: 70 |  |  |  | Complying | Complying |  | 7.65 | 90 | 300 |  | 172 | [5 empty] | 21.35 | [13 empty] | -
[11 empty] | 03.04.2026 | 40 dt. 17.04.2026 |  | 1: 7.73; 2: 8.6; 3: 44; 5: 16; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 7.34 | 135 | 472 |  | 208 | [5 empty] | 15.78 | [13 empty] | -
[11 empty] | 08.05.2026 | 219 dt. 14.05.2026 |  | 1: 7.94; 2: 7.2; 3: 36; 5: 10; 11: 2.95; 25: 80 |  |  |  | Complying | Complying |  | 7.9 | 84 | 324 |  | 158 | [5 empty] | 22.96 | [13 empty] | -
[11 empty] | 03.06.2026 | 422 dt. 15.06.2026 |  | 1: 7.7; 2: 5.4; 3: 28; 5: 8; 11: 6.28; 25: 50 |  |  |  | Complying | Complying |  | 7.38 | 78 | 260 |  | 198 | [5 empty] | 15.85 | [13 empty] | 1.09 X105
[11 empty] | 02.07.2026 | 576 dt. 10.07.2026 | 1126.34 | 1: 7.36; 2: 7.8; 3: 48; 5: 12; 11: 3.96; 25: 60; 52: BDL |  |  |  | Complying | Complying | 1180.12 | 7.09 | 105 | 364 |  | 125 | [5 empty] | 18.22 | [13 empty] | 1.02 X105 | [26 empty] | 19.5
17 | (KUK-STP-003) 15 MLD STP, Sector-6, Urban Estate, Thanesar, Kurukshetra by HUDA in 2020
[11 empty] | 09.01.2026 | 4262 dt. 21.01.2026 | 7.61 | 1: 7.29; 2: 6.2; 3: 44; 5: 15; 11: ND |  |  |  | Complying | Complying | - | 7.35 | 135 | 484 |  | 288 | [5 empty] | 14.84 | [13 empty] | -
[11 empty] | 06.02.2026 | 4443 dt. 16.02.2026 |  | 1: 7.39; 2: 8; 3: 48; 5: 17; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 6.87 | 120 | 432 |  | 175 | [5 empty] | 14.53 | [13 empty] | -
[11 empty] | 06.03.2026 | 4650dt. 19.03.2026 | 653.01 | 1: 8.3; 2: 6.6; 3: 44; 5: 11; 11: ND; 25: 90 |  |  |  | Complying | Complying | 657.41 | 7.55 | 170 | 596 |  | 225 | [5 empty] | 18.75 | [13 empty] | -
[11 empty] | 02.04.2026 | 39 dt. 17.04.2026 | 2.443 | 1: 8.12; 2: 7.8; 3: 40; 5: 15; 11: ND; 25: 80 |  |  |  | Complying | Complying | - | 7.17 | 112 | 388 |  | 168 | [5 empty] | 15.23 | [13 empty] | -
[11 empty] | 08.05.2026 | 218 dt. 14.05.2026 |  | 1: 7.75; 2: 5.4; 3: 28; 5: 13; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 7.94 | 82 | 308 |  | 158 | [5 empty] | 18.28 | [13 empty] | -
[11 empty] | 03.06.2026 | 419 dt. 15.06.2026 | 530.21 | 1: 7.56; 2: 4.8; 3: 28; 5: 7; 11: 7.82; 25: 90 |  |  |  | Complying | Complying |  | 7.28 | 90 | 296 |  | 108 | [5 empty] | 19.27 | [13 empty] | 1.35X105
[11 empty] | 02.07.2026 | 575 dt. 10.07.2026 | 576.99 | 1: 7.53; 2: 6.5; 3: 44; 5: 9; 11: 4.92; 25: 50; 52: BDL |  |  |  | Complying | Complying | 597.2 | 6.85 | 98 | 316 |  | 108 | [5 empty] | 19.52 | [13 empty] | 1.32X105 | [26 empty] | 18.5
18 | (KUK-STP-004) 8 MLD STP Model Town , Pehowa Kurukshetra by PHED in May, 2015 |  | 20 | 7 to 8.50 | 100 | 40 | [68 empty] | 7.3 | 120 | 484 |  | 189 | [5 empty] | 15.09 |  |  | 0.35
[11 empty] | 09.01.2026 | 4264 dt. 21.01.2026 |  | 1: 7.78; 2: 78; 3: 296; 5: 115; 11: 9.28 |  |  |  | Non-Complying | Non-Complying |  | 7.63 | 120 | 392 |  | 185 | [5 empty] | 17.36
[11 empty] | 06.02.2026 | 4444 dt. 16.02.2026 |  | 1: 7.48; 2: 15; 3: 80; 5: 34; 11: 7.89; 25: 400 |  |  |  | Non-Complying | Non-Complying |  | 7.4 | 108 | 400 |  | 146 | [5 empty] | 15.08 | [13 empty] | -
[11 empty] | 06.03.2026 | 4648 dt. 19.03.2026 |  | 1: 7.7; 2: 15; 3: 60; 5: 22; 11: 5.32; 25: 400 |  |  |  | Non-Complying | Non-Complying |  | 8.13 | 112 | 384 |  | 172 | [5 empty] | 16.98 | [13 empty] | -
[11 empty] | 07.04.2026 | 67 dt. 23.04.2026 | 17297.417 | 1: 7.04; 2: 21; 3: 108; 5: 39; 11: ND; 25: 900 |  |  |  | Non-Complying | Non-Complying | - | 6.52 | 135 | 480 |  | 176 | [5 empty] | 15.76 | [13 empty] | -
[11 empty] | 08.05.2026 | 222 dt. 14.05.2026 |  | 1: 8.17; 2: 5.8; 3: 36; 5: 13; 11: 1.768; 25: 90 |  |  |  | Complying | Complying |  | 7.62 | 120 | 404 |  | 156 | [5 empty] | 22.75 | [13 empty] | -
[11 empty] | 03.06.2026 | 422 dt. 15.06.2026 | 1101.41 | 1: 7.7; 2: 5.4; 3: 28; 5: 8; 11: 6.28; 25: 50 |  |  |  | Complying | Complying | 1139.371 | 7.38 | 78 | 260 |  | 198 | [5 empty] | 15.85 | [13 empty] | 1.09X105
[11 empty] | 03.07.2026 | 574 dt. 10.07.2026 | 152.37 | 1: 8.62; 2: 4.6; 3: 24; 5: 8; 11: 2.74; 25: 70; 52: BDL |  |  |  | Complying | Complying | - | 6.74 | 165 | 568 |  | 185 | [5 empty] | 15.68 | [13 empty] | 1.24X105 | [26 empty] | 22
19 | (KUK-STP-005) 11.5 MLD STP Ladwa Road, Shahbad Kurukshetra by PHED in May, 2016 |  | 10 | 7 to 8 | 100 | 10 | [78 empty] | 11.16 |  |  | 0.31
[11 empty] | 09.01.2026 | 4263 dt. 21.01.2026 | 2.81 | 1: 7.38; 2: 6.2; 3: 40; 5: 16; 11: ND |  |  |  | Complying | Complying |  | 6.96 | 125 | 492 |  | 208 | [5 empty] | 13.43
[11 empty] | 10.02.2026 | 4466 dt. 23.02.2026 |  | 1: 7.6; 2: 6.2; 3: 40; 5: 11; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 7.03 | 125 | 440 |  | 285 | [5 empty] | 14.76 | [13 empty] | -
[11 empty] | 06.03.2026 | 4652 dt. 19.03.2026 | 0.19 L/Sec | 1: 7.79; 2: 4.8; 3: 32; 5: 8; 11: ND; 25: 50 |  |  |  | Complying | Complying | 866 (m3/hr) | 7.15 | 390 | 1328 |  | 1235 | [5 empty] | 14.58 | [13 empty] | -
[11 empty] | 07.04.2026 | 68 dt. 23.04.2026 | 1646206 | 1: 7.15; 2: 6.2; 3: 32; 5: 13; 11: ND; 25: 80 |  |  |  | Complying | Complying | - | 6.86 | 135 | 452 |  | 168 | [5 empty] | 14.72 | [13 empty] | -
[11 empty] | 08.05.2026 | 223 dt. 14.05.2026 |  | 1: 7.9; 2: 7; 3: 40; 5: 12; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 7.72 | 125 | 436 |  | 178 | [5 empty] | 18.68 | [13 empty] | -
[11 empty] | 03.06.2026 | 420 dt. 15.06.2026 | 451 | 1: 7.6; 2: 7.2; 3: 44; 5: 14; 11: 8.82; 25: 70 |  |  |  | Complying | Complying | 113 | 7.38 | 86 | 280 |  | 112 | [5 empty] | 23.15 | [13 empty] | 1.12X105
[11 empty] | 03.07.2026 | 571 dt. 10.07.2026 |  | 1: 7.62; 2: 4.2; 3: 16; 5: 7; 11: 1.98; 25: 50; 52: BDL |  |  |  | Complying | Complying |  | 6.83 | 110 | 356 |  | 195 | [5 empty] | 21.95 | [13 empty] | 1.16X105 | [26 empty] | 20
20 | 3 MLD STP Ismailabad, Kurukshetra by PHED July, 2026 | [9 empty] | 03.07.2026 | 572 dt. 10.07.2026 |  | 1: 7.23; 2: 5.2; 3: 28; 5: 8; 11: 3.28; 25: 60; 52: BDL |  |  |  | Complying | Complying |  | 6.97 | 110 | 356 |  | 152 | [5 empty] | 23.96 | [13 empty] | 1.13 X105 | [26 empty] | 24
Panchkula
21 | (PKL-STP-001) 18 MLD STP Panchkula by HUDA in 31.12.2002 |  | <30 | 7-8 | <250 | <100 |  |  |  | 1000 MPN
[11 empty] | 01.01.2026 | 4179 dt. 09.01.2026 |  | 1: 8.01; 2: 7.5; 3: 48; 5: 11; 11: ND |  |  |  | Complying | Complying | - | 7.1 | 110 | 380 |  | 289 | [5 empty] | 13.29
[11 empty] | 12.02.2026 | 4514 dated 02.03.2026 |  | 1: 8.36; 2: 7; 3: 36; 5: 12; 11: ND; 25: 80 |  |  |  | Complying | Complying | - | 7.92 | 145 | 480 |  | 256 | [5 empty] | 17.28 | [13 empty] | -
[11 empty] | 05.03.2026 | 4638 dated 19.03.2026 |  | 1: 8.26; 2: 5.8; 3: 32; 5: 13; 11: ND; 25: 70 |  |  |  | Complying | Complying |  | 7.52 | 130 | 456 |  | 218 | [5 empty] | 19.35 | [13 empty] | -
[11 empty] | 06.04.2026 | 50 dated 22.04.2026 |  | 1: 7.23; 2: 6.2; 3: 40; 5: 11; 11: ND; 25: 60 |  |  |  | Complying | Complying |  | 7.38 | 98 | 312 |  | 178 | [5 empty] | 14.56 | [13 empty] | -
[11 empty] | 06.05.2026 | 184 dt. 13.05.2026 |  | 1: 8.18; 2: 7.5; 3: 36; 5: BDL (DL = 05); 11: ND; 25: 70 |  |  |  | Complying | Complying |  | 7.61 | 170 | 560 |  | 240 | [5 empty] | 21.98 | [13 empty] | -
[11 empty] | 06.05.2026 | 184 dt. 13.05.2026 |  | 1: 8.18; 2: 7.5; 3: 36; 5: BDL (DL = 05); 11: ND |  |  |  | Complying | Complying |  | 7.61 | 170 | 560 |  | 240 | [5 empty] | 21.98
[11 empty] | 10.06.2026 | 484 dated 23.06.2026 |  | 1: 8.02; 2: 3; 3: 16; 5: 4; 11: 2.14; 25: ND |  |  |  | Complying | Complying | - | 8.07 | 84 | 256 |  | 124 | [5 empty] | 54.19
[11 empty] | 01.07.2026 | 557 dt. 09.07.2026 |  | 1: 7.76; 2: 12; 3: 60; 5: 19; 11: 30.82; 25: 500 |  |  |  | Non-Complying | Non-Complying |  | 7.06 | 88 | 352 |  | 188 | [5 empty] | 181.41 | [13 empty] | 1.32X105
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 708 dt. 04.08.2026 |  | 1: 7.05; 2: 6.4; 3: 36; 5: 18; 6: 430; 7: 28.99; 9: 39.04; 12: BDL(DL=0.5); 13: 1.73; 14: ND; 16: ND; 17: ND; 18: 41.3; 19: 106; 20: 74; 23: 116; 24: 180; 25: 50; 28: 0.34; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: 1.324; 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: BDL(DL=02); 55: 786 |  |  |  | Complying | Complying |  | 6.95 | 80 | 264 |  | 138 | 1050 | 70.97 |  | 359.93 |  |  | 17.34 | 20.83 | 4.97 |  | 12.6 | ND | 51.6 | 138 | 90 |  |  | 408 | 228 | 1.34X105 |  |  | 2.86 |  |  | 0.387 | 1.083 | 12.928 | 1.083 | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | 0.732 | BDL(DL=0.001) | [8 empty] | 19.5 |  |  | 1920
22 | (PKL-STP-002) 39 MLD STP Panchkula by HUDA in Nov. 2011 |  | <30 | 7-8 | <250 | <100 |  |  |  | 1000 MPN | [74 empty] | 8.78 |  |  | 0.15
[11 empty] | 01.01.2026 | 4178 dt. 09.01.2026 |  | 1: 7.16; 2: 12; 3: 60; 5: 28; 11: 7.12 |  |  |  | Non-Complying | Non-Complying |  | 7.09 | 140 | 504 |  | 254 | [5 empty] | 17.39
[11 empty] | 12.02.2026 | 4513, 02.03.2026 | - | 1: 8.4; 2: 7.8; 3: 48; 5: 15; 11: ND; 25: 70 |  |  |  | Complying | Complying |  | 7.7 | 102 | 340 |  | 192 | [5 empty] | 14.98 | [13 empty] | -
[11 empty] | 05.03.2026 | 4642 dated 19.03.2026 |  | 1: 8.59; 2: 6.4; 3: 32; 5: 13; 11: ND; 25: 50 |  |  |  | Complying | Complying |  | 7.05 | 110 | 380 |  | 260 | [5 empty] | 12.09
[11 empty] | 06.04.2026 | 51 dated 22.04.2026 |  | 1: 7.34; 2: 5.8; 3: 36; 5: 13; 11: ND; 25: 60 |  |  |  | Complying | Complying |  | 7.06 | 135 | 452 |  | 245 | [5 empty] | 14.79 | [13 empty] | -
[11 empty] | 06.05.2026 | 185 dt. 13.05.2026 |  | 1: 8.29; 2: 8; 3: 36; 5: 12; 11: ND; 25: 50 |  |  |  | Complying | Complying |  | 7.6 | 184 | 576 |  | 332 | [5 empty] | 24.28
[11 empty] | 06.05.2026 | 185 dt. 13.05.2026 |  | 1: 8.29; 2: 8; 3: 36; 5: 12; 11: ND; 25: 50 |  |  |  | Complying | Complying |  | 7.6 | 184 | 576 |  | 332 | [5 empty] | 24.28
[11 empty] | 10.06.2026 | 483 dt. 23.06.2026 |  | 1: 8; 2: 3; 3: 16; 5: 4; 11: 2.16; 25: ND |  |  |  | Complying | Complying |  | 7.96 | 104 | 348 |  | 175 | [5 empty] | 63.08 | [13 empty] | 1.8x3
[11 empty] | 01.07.2026 | 556 dt. 09.07.2026 |  | 1: 7.34; 2: 4.5; 3: 24; 5: 7; 11: 8.4; 25: ND |  |  |  | Complying | Complying |  | 7.37 | 84 | 264 |  | 98 | [5 empty] | 164.73 | [13 empty] | 1.8X105
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 709 dt. 04.08.2026 |  | 1: 7.44; 2: 7.2; 3: 36; 5: 10; 6: 352; 7: 77.97; 9: 40.87; 12: BDL(DL=0.5); 13: BDL(DL=0.5); 14: ND; 16: ND; 17: ND; 18: 32.8; 19: 114; 20: 74; 23: 124; 24: 188; 25: 70; 28: 1.03; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: 0.348; 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: BDL(DL=02); 55: 640 |  |  |  | Complying | Complying |  | 7.05 | 110 | 368 |  | 156 | 890 | 85.97 |  | 428.47 |  |  | 16.48 | 8.26 | 3.24 |  | 8 | ND | 54.5 | 146 | 98 |  |  | 428 | 244 | 1.36X105 |  |  | 1.5 |  |  | 0.408 | BDL(DL=0.230) | 9.286 | 0.314 | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | 0.732 | BDL(DL=0.001) | [8 empty] | 21 |  |  | 1623
23 | (PKL-STP-003) 15 MLD STP Sector- 28, Panchkula by HUDA in 2012 | PHED | <10 | 7-8 | - | <10 |  |  |  | 1000 MPN
[11 empty] | 01.01.2026 | 4180 dt. 09.01.2026 |  | 1: 7.74; 2: 8; 3: 44; 5: 15; 11: 2.93 |  |  |  | Complying | Complying |  | 6.87 | 120 | 388 |  | 183 | [5 empty] | 14.79
[11 empty] | 12.02.2026 | 4515 dated 02.03.2026 | 38546910 | 1: 8.42; 2: 7.5; 3: 44; 5: 13; 11: ND; 25: 80 |  |  |  | Complying | Complying | 62728400 | 7.28 | 120 | 432 |  | 218 | [5 empty] | 14.68 | [13 empty] | -
[11 empty] | 05.03.2026 | 4639 dated 19.03.20260 | 38824060 | 1: 8.49; 2: 5.2; 3: 28; 5: 9; 11: ND; 25: 70 |  |  |  | Complying | Complying | 66417110 | 7.95 | 102 | 340 |  | 212 | [5 empty] | 17.63 | [13 empty] | -
[11 empty] | 06.04.2026 | 52 dated 22.04.2026 | - | 1: 7.53; 2: 5.8; 3: 36; 5: 9; 11: ND; 25: 80 |  |  |  | Complying | Complying | - | 7.25 | 120 | 396 |  | 182 | [5 empty] | 12.72 | [13 empty] | -
[11 empty] | 08.05.2026 | 216 dt. 18.05.2026 | 39603610 | 1: 8.06; 2: 5.2; 3: 28; 5: 7.5; 11: ND |  |  |  | Complying | Complying | 68436820 | 8.1 | 84 | 284 |  | 103 | [5 empty] | 17.29
[11 empty] | 08.05.2026 | 216 dt. 18.05.2026 | 39603610 | 1: 8.06; 2: 5.2; 3: 28; 5: 7.5; 11: ND |  |  |  | Complying | Complying | 68436820 | 8.1 | 84 | 284 |  | 103 | [5 empty] | 17.29
[11 empty] | 10.06.2026 | 485 dated 23.06.2026 |  | 1: 8.67; 2: 6; 3: 32; 5: 9; 11: 4.87; 25: 50 |  |  |  | Complying | Complying |  | 7.83 | 78 | 248 |  | 111 | [5 empty] | 40.1 | [13 empty] | -
[11 empty] | 01.07.2026 | 553 dt. 09.07.2026 | 40412720 | 1: 7.39; 2: 4.5; 3: 28; 5: 8; 11: 11.2; 25: 50 |  |  |  | Complying | Complying | 70208510 | 7.38 | 90 | 280 |  | 137 | [5 empty] | 105.07 | [13 empty] | 1.76X105
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 711 dt. 04.08.2026 |  | 1: 7.46; 2: 7.5; 3: 36; 5: 11; 6: 408; 7: 43.98; 9: 54.22; 12: BDL(DL=0.5); 13: BDL(DL=0.5); 14: ND; 16: ND; 17: ND; 18: 56.9; 19: 116; 20: 78; 23: 120; 24: 194; 25: 80; 28: 1.76; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: BDL(DL=0.264); 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: BDL(DL=02); 55: 743 |  |  |  | Complying | Complying |  | 7.64 | 62 | 220 |  | 172 | 920 | 61.98 |  | 425.13 |  |  | 17.84 | 7.83 | 3.94 |  | 4.8 | ND | 775.2 | 136 | 92 |  |  | 484 | 228 | 1.29X105 |  |  | 2.15 |  |  | BDL(DL=0.001) | BDL(DL=0.230) | 4.234 | 0.1842 | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | BDL(DL=0.5243) | BDL(DL=0.001) | [8 empty] | 18.5 |  |  | 1680
24 | (PKL-STP-004) 4.5 MLD Kalka Panchkula by PHED in 30.3.2015 |  | 20 | 7 to 8.50 | 100 | 40
[11 empty] | 05.01.2026 | 4201 dt. 15.01.2026 |  | 1: 8.02; 2: 15; 3: 84; 5: 25; 11: 9.28 |  |  |  | Non-Complying | Non-Complying |  | 6.87 | 125 | 420 |  | 188 | [5 empty] | 17.26
[11 empty] | 10.02.2026 | 4491 dt. 24.02.2026 | 1.3 | 1: 7.64; 2: 14; 3: 76; 5: 25; 11: 8.85 |  |  |  | Non-Complying | Non-Complying | 1.3 | 7.9 | 110 | 400 |  | 289 | [5 empty] | 13.89 | [13 empty] | -
| Mar., 2026 | [9 empty] | 06.03.2026 | 4643 dated 19.03.2026 |  | 1: 7.97; 2: 14; 3: 64; 5: 29; 11: 7.24; 25: 600 |  |  |  | Non-Complying | Non-Complying |  | 7.45 | 135 | 436 |  | 188 | [5 empty] | 16.38 | [13 empty] | -
| Apr.,2026 | [9 empty] | 02.04.2026 | 30 dated 17.04.2026 | 1.3 | 1: 7.77; 2: 13; 3: 64; 5: 64; 11: 7.84; 25: 64 |  |  |  | Non-Complying | Non-Complying | 1.3 | 7.45 | 120 | 396 |  | 210 | [5 empty] | 14.68 | [13 empty] | -
[11 empty] | 13.05.2026 | 253 dt. 26.05.2026 | 1.3 | 1: 8.18; 2: 9.2; 3: 48; 5: 15; 11: 9.822; 25: 90 |  |  |  | Complying | Complying | 1.3 | 7.76 | 220 | 712 |  | 185 | [5 empty] | 64.446
[11 empty] | 08.06.2026 | 458 dated 22.06.2026 |  | 1: 8.2; 2: 7.2; 3: 44; 5: 16; 11: 7.26; 25: 90 |  |  |  | Complying | Complying |  | 7.78 | 120 | 408 |  | 205 | [5 empty] | 31.79 | [13 empty] | -
[11 empty] | 03.07.2026 | 578 dt. 10.07.2026 |  | 1: 7.75; 2: 7.8; 3: 44; 5: 15; 11: 6.27; 25: 90 |  |  |  | Complying | Complying |  | 7.08 | 110 | 376 |  | 182 | [5 empty] | 15.76 | [13 empty] | 1.15X105
25 | (PKL-STP-005) 0.25 MLD Kalka Panchkula by PHED in 28.5. 2017 |  | 10 | 7 to 8.50 | 100 | 50
[11 empty] | 05.01.2026 | 4200 dt. 15.01.2026 |  | 1: 7.82; 2: 7.8; 3: 48; 5: 13; 11: 8.22 |  |  |  | Complying | Complying |  | 6.94 | 120 | 424 |  | 208 | [5 empty] | 14.56
[11 empty] | 10.02.2026 | 4492 dt. 24.02.2026 | 0.25 | 1: 8.06; 2: 18; 3: 92; 5: 32; 11: 7.42 |  |  |  | Non-Complying | Non-Complying | 0.25 | 7.96 | 130 | 452 |  | 277 | [5 empty] | 12.89 | [13 empty] | -
| Mar., 2026 | [9 empty] | 06.03.2026 | 4644 dated 19.03.2026 |  | 1: 8.64; 2: 7.2; 3: 48; 5: 12; 11: -; 25: 80 |  |  |  | Complying | Complying |  | 8.38 | 140 | 448 |  | 205 | [5 empty] | 17.47 | [13 empty] | -
| Apr.,2026 | [9 empty] | 02.04.2026 | 29 dated 17.04.2026 | - | 1: 8.73; 2: 7.8; 3: 48; 5: 17; 11: ND; 25: 90 |  |  |  | Complying | Complying | - | 8.67 | 102 | 340 |  | 195 | [5 empty] | 12.96 | [13 empty] | -
[11 empty] | 15.05.2026 | 256 dt. 26.05.2026 |  | 1: 8.27; 2: 4.5; 3: 24; 5: 8; 11: 5.643; 25: ND |  |  |  | Complying | Complying |  | 7.63 | 104 | 336 |  | 150 | [5 empty] | 31.328 | [13 empty] | -
[11 empty] | 08.06.2026 | 459 dated 22.06.2026 | - | 1: 8.12; 2: 6.2; 3: 32; 5: 9; 11: 8.09; 25: 70 |  |  |  | Complying | Complying | 5.2 | 7.6 | 140 | 504 |  | 285 | [5 empty] | 29.76 | [13 empty] | -
[11 empty] | 03.07.2026 | 578-A dt. 10.07.2026 |  | 1: 8.44; 2: 7; 3: 32; 5: 10; 11: BDL; 25: 80 |  |  |  | Complying | Complying |  | 7.83 | 120 | 392 |  | 185 | [5 empty] | 17.24 | [13 empty] | 1.22X105
Pinjore
26 | (PKL-STP-006) 5 MLD STP Nalagarh Road, Manakpur, Pinjore Panchkula by PHED 31.1.2015 | PHED | 10 | 7 to 8 | 50 | 20
[11 empty] | 28.01.2026 | 4370 dt. 09.02.2026 |  | 1: 7.08; 2: 6.5; 3: 44; 5: 15; 11: ND |  |  |  | Complying | Complying |  | 6.98 | 140 | 492 |  | 208 | [5 empty] | 12.72
| Feb.,2026 | [9 empty] | 19.02.2026 | 4550 dated 03.03.2026 | - | 1: 7.64; 2: 5.8; 3: 32; 5: 9; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 7.05 | 120 | 408 |  | 175 | [5 empty] | 14.58 | [13 empty] | -
| Mar., 2026 | [9 empty] | 12.03.2026 | 4701, 25.03.2026 |  | 1: 8.09; 2: 5.4; 3: 28; 5: 8.5; 11: ND; 25: 90 |  |  |  | Complying | Complying | - | 7.6 | 122 | 396 |  | 212 | [5 empty] | 17.96 | [13 empty] | -
| Apr.,2026 | [9 empty] | 09.04.2026 | 28.04.2026 |  | 1: 8.12; 2: 6.8; 3: 44; 5: 13; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 7.75 | 106 | 340 |  | 118 | [5 empty] | 13.28 | [13 empty] | -
[11 empty] | 13.05.2026 | 252 dt. 26.05.2026 | 0.74 | 1: 8.15; 2: 12; 3: 56; 5: 17; 11: 13.217; 25: 3500 |  |  |  | Complying | Complying | 0.81 | 7.99 | 210 | 652 |  | 237 | [5 empty] | 51.837
[11 empty] | 10.06.2026 | 478 dated 22.06.2026 | 25.22 | 1: 8.27; 2: 5.8; 3: 28; 5: 10; 11: 5.34; 25: 80 |  |  |  | Complying | Complying | 28.9 | 7.97 | 102 | 340 |  | 172 | [5 empty] | 18.76 | [13 empty] | -
[11 empty] | 03.07.2026 | 577 dt. 10.07.2026 |  | 1: 7.62; 2: 18; 3: 96; 5: 32; 11: 12.92; 25: 600 |  |  |  | Non-Complying | Non-Complying |  | 7.09 | 96 | 324 |  | 32 | [5 empty] | 24.93 | [13 empty] | 1.36X105
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 713 dt. 04.08.2026 |  | 1: 7.53; 2: 58; 3: 208; 5: 95; 6: 602; 7: 51.98; 9: 77.57; 12: BDL(DL=0.5); 13: 2.34; 14: ND; 16: ND; 17: ND; 18: 5.8; 19: 118; 20: 96; 23: 132; 24: 214; 25: 90; 28: 0.46; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: BDL(DL=0.264); 34: 0.1322; 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: 7; 55: 1104 |  |  |  | Non-Complying | Non-Complying |  | 7.12 | 120 | 396 |  | 158 | 670 | 201.93 |  | 409.78 |  |  | 12.32 | 13.93 | 5.98 |  | 16 | ND | 53.4 | 156 | 228 |  |  | 328 | 384 | 1.24X105 |  |  | 2.58 |  |  | BDL(DL=0.001) | BDL(DL=0.230) | 5.928 | 0.9396 | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | 0.8394 | BDL(DL=0.001) | [8 empty] | 18 |  |  | 1231
27 | (PKL-STP-007) 9 MLD STP Garrison Engineer , Chandimandir Panchkula in April 2012
[11 empty] | 28.01.2026 | 4369 dt. 09.02.2026 |  | 1: 7.18; 2: 7.5; 3: 40; 5: 12; 11: 1.84 |  |  |  | Complying | Complying |  | 7.09 | 125 | 408 |  | 128 | [5 empty] | 14.57
[11 empty] | 19.02.2026 | 4551 dt. 03.03.2026 |  | 1: 7.86; 2: 5.8; 3: 32; 5: 11; 11: ND; 25: 70 |  |  |  | Complying | Complying | 87.1 | 7.29 | 110 | 392 |  | 172 | [5 empty] | 13.52 | [13 empty] | -
[11 empty] | 12.03.2026 | 4700 dt. 25.03.2026 |  | 1: 7.4; 2: 8.4; 3: 44; 5: 8.5; 11: -; 25: 70 |  |  |  | Complying | Complying |  | 6.88 | 125 | 404 |  | 205 | [5 empty] | 14.76 | [13 empty] | -
[11 empty] | 09.04.2026 | 104 dt. 28.04.2026 |  | 1: 8.09; 2: 8.6; 3: 48; 5: 17; 11: ND; 25: 90 |  |  |  | Complying | Complying | 110 | 7.5 | 108 | 368 |  | 248 | [5 empty] | 11.98 | [13 empty] | -
[11 empty] | 27.05.2026 | 356 dt. 10.06.2026 |  | 1: 7.9; 2: 9.2; 3: 48; 5: 17; 11: 11.2; 25: 90 |  |  |  | Complying | Complying | 110 | 7.82 | 588 | 1840 |  | 478 | [5 empty] | 257.784 | [13 empty] | -
[11 empty] | 10.06.2026 | 479 dt. 22.06.2026 |  | 1: 7.97; 2: 9.5; 3: 48; 5: 26; 11: 15.83; 25: 200 |  |  |  | Complying | Complying | 95 | 7.9 | 160 | 552 |  | 308 | [5 empty] | 121-42 | [13 empty] | -
[11 empty] | 03.07.2026 | 578 dt. 10.07.2026 | - | 1: 7.51; 2: 9.2; 3: 48; 5: 18; 11: 1.08; 25: 70 |  |  |  | Complying | Complying |  | 7.24 | 108 | 352 |  | 135 | [5 empty] | 21.28 | [13 empty] | 1.11X105
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 714 dt. 04.08.2026 |  | 1: 7; 2: 9.2; 3: 48; 5: 18; 6: 378; 7: 94.97; 9: 186.04; 12: BDL(DL=0.5); 13: 5.08; 14: 0.92; 16: ND; 17: ND; 18: 15.8; 19: 112; 20: 128; 23: 690; 24: 240; 25: 90; 28: 1.24; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: BDL(DL=0.264); 34: 1.942; 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: BDL(DL=0.5); 55: 690 |  |  |  | Non-Complying | Non-Complying |  | 6.88 | 380 | 1264 |  | 708 | 932 | 224.93 |  | 356.3 |  |  | 23.96 | 15.93 | 7.24 |  | 9.6 | ND | 142.6 | 136 | 216 |  |  | 1696 | 352 | 1.82X105 |  |  | 3.28 |  |  | 0.106 | BDL(DL=0.230) | 5.248 | 1.942 | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | BDL(DL=0.5243) | BDL(DL=0.001) | [8 empty] | 28.5 |  |  | 1696
28 | (PKL-STP-008) 0.75 MLD STP, Khatoli, Panchkula by ULBD in 31.10.2021
[11 empty] | 05.01.2026 | 4205 dt. 15.01.2026 |  | 1: 7.72; 2: 7; 3: 44; 5: 12; 11: ND |  |  |  | Complying | Complying |  | 7.42 | 125 | 408 |  | 198 | [5 empty] | 14.24
[11 empty] | 03.02.2026 | 4432 dated 16.02.2026 |  | 1: 8.18; 2: 7.6; 3: 44; 5: 12; 11: ND; 25: 70 |  |  |  | Complying | Complying |  | 7.36 | 110 | 376 |  | 148 | [5 empty] | 17.33
[11 empty] | 10.03.2026 | 4686 dated 24.03.2026 |  | 1: 8.08; 2: 4.5; 3: 24; 5: 6; 11: BDL; 25: ND |  |  |  | Complying | Complying |  | 7.66 | 120 | 380 |  | 184 | [5 empty] | 17.26 | [13 empty] | -
[11 empty] | 15.04.2026 | 121 dated 28.04.2026 |  | 1: 8.41; 2: 6.4; 3: 36; 5: 12; 11: ND; 25: 60 |  |  |  | Complying | Complying | - | 7.73 | 102 | 360 |  | 138 | [5 empty] | 14.24 | [13 empty] | -
[11 empty] | 07.05.2026 | 200 dt. 14.05.2026 |  | 1: 8.09; 2: 9.2; 3: 48; 5: 14; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 8.03 | 92 | 296 |  | 104 | [5 empty] | 14.68 | [13 empty] | -
[11 empty] | 09.06.2026 | 464 dated 22.06.2026 |  | 1: 8.4; 2: 5.6; 3: 36; 5: 9; 11: 7.22; 25: 90 |  |  |  | Complying | Complying |  | 7.6 | 140 | 460 |  | 235 | [5 empty] | 28.95 | [13 empty] | -
[11 empty] | 08.07.2026 | 626 dt.15.07.2026 |  | 1: 7.78; 2: 4.2; 3: 24; 5: 9; 11: 1.21; 25: 50 |  |  |  | Complying | Complying |  | 7.32 | 102 | 380 |  | 189 | [5 empty] | 12.6 | [13 empty] | 1.24X106
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 697 dt. 04.08.2026 |  | 1: 8.13; 2: 5.2; 3: 32; 5: 9; 6: 340; 7: 41.98; 9: 37.37; 12: BDL(DL=0.5); 13: ND; 14: ND; 16: ND; 17: ND; 18: 39.9; 19: 116; 20: 76; 23: 120; 24: 192; 25: 60; 28: 1.1; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: BDL(DL=0.264); 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: BDL(DL=02); 55: 636 |  |  |  | Complying | Complying |  | 7.69 | 90 | 288 |  | 128 | 842 | 128.96 |  | 357.89 |  |  | 17.23 | 11.93 | 4.25 |  | 11.2 | ND | 114.4 | 146 | 98 |  |  | 312 | 244 | 1.28X105 |  |  | 3.56 |  |  | 0.208 | 0.9382 | 3.682 | 0.9822 | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | BDL(DL=0.5243) | BDL(DL=0.001) | [8 empty] | 14 |  |  | 1540
29 | (PKL-STP-009) 0.75 MLD STP, Billa, Panchkula by ULBD in 31.10.2021
[11 empty] | 05.01.2026 | 4204 dt. 15.01.2026 |  | 1: 7.3; 2: 6.2; 3: 40; 5: 12; 11: ND |  |  |  | Complying | Complying |  | 6.26 | 120 | 396 |  | 186 | [5 empty] | 13.24
[11 empty] | 04.02.2026 | 4434 dated 16.02.2026 | - | 1: 7.86; 2: 7.5; 3: 48; 5: 16; 11: ND; 25: 50 |  |  |  | Complying | Complying |  | 7.05 | 108 | 396 |  | 182 | [5 empty] | 13.78 | [13 empty] | -
[11 empty] | 10.03.2026 | 4683 dated 24.03.2026 |  | 1: 7.84; 2: 28; 3: 104; 5: 23; 11: BDL; 25: 600 |  |  |  | Non-Complying | Non-Complying |  | 7.89 | 120 | 388 |  | 210 | [5 empty] | 16.72 | [13 empty] | -
[11 empty] | 15.04.2026 | 123 dated 28.04.2026 | 612 | 1: 7.79; 2: 5.8; 3: 32; 5: 7; 11: ND; 25: 70 |  |  |  | Complying | Complying | 433752 | 7.74 | 98 | 320 |  | 192 | [5 empty] | 13.72 | [13 empty] | -
[11 empty] | 07.05.2026 | 201 dt. 14.05.2026 | 612 | 1: 8.03; 2: 4.8; 3: 20; 5: 5; 11: ND |  |  |  | Complying | Complying |  | 8.08 | 84 | 288 |  | 92 | [5 empty] | 17.54 | [13 empty] | -
[11 empty] | 09.06.2026 | 462 dated 22.06.2026 | 612 | 1: 8.44; 2: 7; 3: 44; 5: 13; 11: 5.98; 25: 80 |  |  |  | Complying | Complying | 1433752 | 7.79 | 108 | 360 |  | 176 | [5 empty] | 19.32 | [13 empty] | -
[11 empty] | 08.07.2026 | 624 dt.15.07.2026 |  | 1: 6.88; 2: 40; 3: 144; 5: 72; 11: 14.01; 25: 400 |  |  |  | Non-Complying | Non-Complying
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 700 dt. 04.08.2026 |  | 1: 7.28; 2: 120; 3: 384; 5: 192; 6: 802; 7: 41.98; 9: 520.91; 12: 20.46; 13: 18.93; 14: 7.26; 16: 8; 17: ND; 18: 87.3; 19: 114; 20: 72; 23: 328; 24: 186; 25: 1.42X105; 28: 2.76; 31: BDL(DL=0.001); 32: 0.8234; 33: 4.893; 34: 1.829; 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: 18; 55: 1468 |  |  |  | Non- Complying | Non- Complying
30 | (PKL-STP-010) 0.75 MLD STP, Sukhdarshanpur, Panchkula by ULBD in 30.09.2021
[11 empty] | 05.01.2026 | 4206 dt. 15.01.2026 | 7396 | 1: 7.26; 2: 7.2; 3: 40; 5: 13; 11: ND |  |  |  | Complying | Complying | 85392 | 7.3 | 130 | 420 |  | 260 | [5 empty] | 12.96
[11 empty] | 04.02.2026 | 4435 dated 16.02.2026 |  | 1: 7.93; 2: 7.8; 3: 44; 5: 17; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 7.04 | 125 | 412 |  | 205 | [5 empty] | 14.72 | [13 empty] | 80
[11 empty] | 10.03.2026 | 4685 dated 24.03.2026 |  | 1: 8.27; 2: 5.6; 3: 28; 5: 9 |  |  |  | Complying | Complying
[11 empty] | 15.04.2026 | 119 dated 28.04.2026 | 9707 | 1: 8.03; 2: 8.2; 3: 48; 5: 16; 11: ND; 25: 70 |  |  |  | Complying | Complying | 87876 | 7.79 | 135 | 460 |  | 218 | [5 empty] | 13.24 | [13 empty] | -
[11 empty] | 07.05.2026 | 202 dt. 14.05.2026 | 10255 | 1: 8.02; 2: 4.5; 3: 24; 5: 4; 11: ND; 25: ND |  |  |  | Complying | Complying | 88753 | 7.8 | 72 | 236 |  | 95 | [5 empty] | 19.36 | [13 empty] | -
[11 empty] | 09.06.2026 | 465 dated 22.06.2026 | 11530 | 1: 8.53; 2: 7.8; 3: 44; 5: 16; 11: 7.26; 25: 90 |  |  |  | Complying | Complying | 94734 | 7.8 | 105 | 356 |  | 215 | [5 empty] | 30.72 | [13 empty] | -
[11 empty] | 08.07.2026 | 622 dt.15.07.2026 | 131105 | 1: 7.87; 2: 7.8; 3: 40; 5: 12; 11: ND; 25: 90 |  |  |  | Complying | Complying | 92004 | 6.8 | 120 | 412 |  | 265 | [5 empty] | 14.01 | [13 empty] | 1.28X105
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 696 dt. 04.08.2026 |  | 1: 8.3; 2: 5.8; 3: 36; 5: 7; 6: 340; 7: 77.97; 9: 39.04; 12: BDL(DL=0.5); 13: ND; 14: ND; 16: ND; 17: ND; 18: 39.3; 19: 108; 20: 70; 23: 132; 24: 178; 25: 60; 28: 1.13; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: BDL(DL=0.264); 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: BDL(DL=02); 55: 623 |  |  |  | Complying | Complying |  | 7.78 | 105 | 352 |  | 117 | 570 | 147.95 |  | 357.89 |  |  | 23.96 | 23.79 | 7.64 |  | 3.6 | ND | 55.8 | 136 | 88 |  |  | 342 | 224 | 1.34X105 |  |  | 1.8 |  |  | 0.294 | 0.348 | 3.982 | 0.7824 | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | BDL(DL=0.5243) | BDL(DL=0.001) | [8 empty] | 22 |  |  | 1037
31 | (PKL-STP-011) 0.5 MLD STP, Nangal & Alipur, Panchkula by ULBD in 31.10.2021
[11 empty] | 05.01.2026 | 4207 dt. 15.01.2026 |  | 1: 7.56; 2: 7.8; 3: 44; 5: 14; 11: ND |  |  |  | Complying | Complying | 134115 | 7.37 | 120 | 432 |  | 175 | [5 empty] | 13.32
[11 empty] | 03.02.2026 | 4430 dated 16.02.2026 |  | 1: 7.99; 2: 7.4; 3: 36; 5: 10; 11: ND; 25: 50 |  |  |  | Complying | Complying |  | 7.29 | 120 | 408 |  | 210 | [5 empty] | 14.78
[11 empty] | 10.03.2026 | 4681 dated 24.03.2026 |  | 1: 8.05; 2: 5.2; 3: 32; 5: 12; 11: ND; 25: 50 |  |  |  | Complying | Complying | 141532 | 8.06 | 110 | 380 |  | 352 | [5 empty] | 14.52 | [13 empty] | -
[11 empty] | 15.04.2026 | 120 dated 28.04.2026 | 2142 | 1: 8.28; 2: 5.2; 3: 28; 5: 9; 11: ND; 25: 60 |  |  |  | Complying | Complying | 136336 | 7.73 | 110 | 368 |  | 196 | [5 empty] | 13.26 | [13 empty] | -
[11 empty] | 07.05.2026 | 198 dt. 14.05.2026 | 5378 | 1: 8.09; 2: 5.4; 3: 28; 5: 7; 11: ND; 25: ND |  |  |  | Complying | Complying | 149070 | 7.86 | 80 | 252 |  | 95 | [5 empty] | 18.34 | [13 empty] | -
[11 empty] | 09.06.2026 | 466 dated 22.06.2026 | 10350 | 1: 8.56; 2: 7.8; 3: 48; 5: 15; 11: 7.08; 25: 90 |  |  |  | Complying | Complying | 153796 | 7.39 | 160 | 540 |  | 312 | [5 empty] | 38.25 | [13 empty] | -
[11 empty] | 08.07.2026 | 627 dt.15.07.2026 | 14857 | 1: 7.89; 2: 5; 3: 28; 5: 16; 11: 5.6; 25: 70 |  |  |  | Complying | Complying | 157970 | 7.43 | 125 | 448 |  | 359 | [5 empty] | 29.42 | [13 empty] | 2.18X106
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 695 dt. 04.08.2026 |  | 1: 7.96; 2: 5.2; 3: 28; 5: 7; 6: 350; 7: 88.97; 9: 42.71; 12: BDL(DL=0.5); 13: 2.33; 14: ND; 16: ND; 17: ND; 18: 38.8; 19: 116; 20: 78; 23: 126; 24: 194; 25: 50; 28: 1.18; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: BDL(DL=0.264); 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: BDL(DL=02); 55: 650 |  |  |  | Complying | Complying |  | 7.4 | 120 | 384 |  | 125 | 810 | 153.95 |  | 357.89 |  |  | 14.96 | 113.42 | 8.82 |  | 8.6 | ND | 109 | 122 | 80 |  |  | 320 | 202 | 1.23X105 |  |  | 3.38 |  |  | 0.312 | BDL(DL=0.230) | 4.238 | 0.9387 | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | BDL(DL=0.5243) | BDL(DL=0.001) | [8 empty] | 23.5 |  |  | 1474
32 | (PKL-STP-012) 0.75 MLD STP, Kot, Panchkula by ULBD in 31.10.2021
[11 empty] | 05.01.2026 | 4203 dt. 15.01.2026 |  | 1: 6.34; 2: 5.8; 3: 36; 5: 10; 11: ND |  |  |  | Complying | Complying |  | 7.6 | 110 | 380 |  | 176 | [5 empty] | 12.76
[11 empty] | 03.02.2026 | 4429 dated 16.02.2026 | - | 1: 8.07; 2: 7.2; 3: 40; 5: 11; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 7.29 | 110 | 380 |  | 172 | [5 empty] | 13.79 | [13 empty] | -
[11 empty] | 10.03.2026 | 4684 dated 24.03.2026 |  | 1: 8.2; 2: 4.4; 3: 24; 5: 8; 11: ND; 25: 50 |  |  |  | Complying | Complying | 431238 | 7.76 | 110 | 376 |  | 184 | [5 empty] | 12.86 | [13 empty] | -
[11 empty] | 15.04.2026 | 122 dated 28.04.2026 | 1997765 | 1: 8.48; 2: 7.8; 3: 44; 5: 13; 11: ND; 25: 90 |  |  |  | Complying | Complying | 155815 | 7.94 | 110 | 388 |  | 175 | [5 empty] | 15.42 | [13 empty] | -
[11 empty] | 07.05.2026 | 203 dt. 14.05.2026 |  | 1: 8.11; 2: 4.5; 3: 24; 5: 7; 11: ND; 25: ND |  |  |  | Complying | Complying |  | 8.01 | 76 | 248 |  | 102 | [5 empty] | 21.32 | [13 empty] | -
[11 empty] | 09.06.2026 | 461 dated 22.06.2026 | 217029 | 1: 8.37; 2: 7.5; 3: 36; 5: 11; 11: 4.82; 25: 50 |  |  |  | Complying | Complying |  | 7.38 | 120 | 392 |  | 198 | [5 empty] | 18.77 | [13 empty] | -
[11 empty] | 08.07.2026 | 625 dt.15.07.2026 | 218432 | 1: 7.55; 2: 5.4; 3: 32; 5: 8; 11: 4.76; 25: 60 |  |  |  | Complying | Complying |  | 7.06 | 102 | 384 |  | 265 | [5 empty] | 23.81 | [13 empty] | 1.26 X105
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 699 dt. 04.08.2026 |  | 1: 7.59; 2: 115; 3: 360; 5: 126; 6: 994; 7: 137.95; 9: 464.51; 12: 20.98; 13: 21.24; 14: 3.82; 16: 8; 17: ND; 18: 56.3; 19: 162; 20: 100; 23: 382; 24: 262; 25: 1.44X105; 28: 1.503; 31: 0.322; 32: 0.9825; 33: 4.927; 34: 0.213; 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: 0.8392; 43: BDL(DL=0.001); 52: 16.5; 55: 1808 |  |  |  | Non- Complying | Non- Complying
33 | (PKL-STP-013) 0.5 MLD STP, Khagesara & Toka, Panchkula by ULBD in 31.10.2021
[11 empty] | 05.01.2026 | 4202 dt. 15.01.2026 |  | 1: 7.89; 2: 5.8; 3: 32; 5: 9; 11: ND |  |  |  | Complying | Complying |  | 7.6 | 125 | 412 |  | 196 | [5 empty] | 13.65
[11 empty] | 03.02.2026 | 4433 dated 16.02.2026 |  | 1: 7.99; 2: 7.2; 3: 40; 5: 11; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 7.17 | 120 | 408 |  | 224 | [5 empty] | 14.28 | [13 empty] | -
[11 empty] | 10.03.2026 | 4682 dated 24.03.2026 |  | 1: 7.98; 2: 5.4; 3: 28; 5: 7; 11: ND; 25: 50 |  |  |  | Complying | Complying |  | 7.56 | 140 | 424 |  | 188 | [5 empty] | 18.24 | [13 empty] | -
[11 empty] | 15.04.2026 | 118 dated 28.04.2026 | 250 | 1: 8.29; 2: 7; 3: 44; 5: 12; 11: ND; 25: 80 |  |  |  | Complying | Complying | 14492 | 7.96 | 130 | 452 |  | 228 | [5 empty] | 12.68 | [13 empty] | -
[11 empty] | 07.05.2026 | 199 dt. 14.05.2026 |  | 1: 8.01; 2: 13; 3: 64; 5: 18; 11: 8.48 |  |  |  | Non-Complying | Non-Complying |  | 7.72 | 120 | 420 |  | 266 | [5 empty] | 19.42 | [13 empty] | -
[11 empty] | 09.06.2026 | 463 dated 22.06.2026 | 391 | 1: 8.52; 2: 7; 3: 40; 5: 12; 11: 6.32; 25: 60 |  |  |  | Complying | Complying | 15123 | 7.91 | 125 | 428 |  | 204 | [5 empty] | 17.38 | [13 empty] | -
[11 empty] | 08.07.2026 | 623 dt.15.07.2026 | 549 | 1: 7.95; 2: 4; 3: 20; 5: 13; 11: 1.1; 25: 90 |  |  |  | Complying | Complying | 154620 | 7.38 | 98 | 344 |  | 289 | [5 empty] | 21.01 | [13 empty] | 1.24X105
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 698 dt. 04.08.2026 |  | 1: 7.78; 2: 5; 3: 28; 5: 6; 6: 342; 7: 27.99; 9: 94.77; 12: 2.24; 13: 1.84; 14: ND; 16: ND; 17: ND; 18: 41; 19: 92; 20: 60; 23: 126; 24: 152; 25: 90; 28: 1.43; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: BDL(DL=0.264); 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: BDL(DL=02); 55: 628 |  |  |  | Complying | Complying |  | 7.9 | 60 | 200 |  | 135 | 772 | 117.96 |  | 414.62 |  |  | 24.96 | 14.95 | 1.93 |  | 9.6 | ND | 103.4 | 130 | 84 |  |  | 344 | 214 | 1.32X105 |  |  | 3.05 |  |  | 0.182 | 0.9382 | 3.298 | 1.232 | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | BDL(DL=0.5243) | BDL(DL=0.001) | [8 empty] | 15 |  |  | 1408
34 | (PKL-STP-014) 1.5 MLD STP, Saketri, Panchkula by ULBD in 30.06.2022
[11 empty] | 01.01.2026 | 4177 dt. 09.01.2026 |  | 1: 8.06; 2: 7.5; 3: 44; 5: 13; 11: ND |  |  |  | Complying | Complying |  | 7.02 | 145 | 492 |  | 296 | [5 empty] | 18.27
[11 empty] | 12.02.2026 | 4511 dated 02.03.2026 |  | 1: 8.42; 2: 7.6; 3: 44; 5: 15; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 7.85 | 110 | 380 |  | 182 | [5 empty] | 13.42 | [13 empty] | -
[11 empty] | 05.03.2026 | 4641 dated 19.03.2026 |  | 1: 8.38; 2: 8; 3: 44; 5: 12; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 7.83 | 112 | 384 |  | 132 | [5 empty] | 12.93 | [13 empty] | -
[11 empty] | 16.04.2026 | 128 dated 29.04.2026 |  | 1: 8.03; 2: 7.5; 3: 48; 5: 13; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 7.98 | 120 | 408 |  | 176 | [5 empty] | 16.32 | [13 empty] | -
[11 empty] | 05.05.2026 | 183 dt. 13.05.2026 | 6708 | 1: 8.31; 2: 9.2; 3: 44; 5: BDL (DL=05); 11: 3.22 |  |  |  | Complying | Complying | 39273 | 8.06 | 160 | 528 |  | 316 | [5 empty] | 12.98
[11 empty] | 09.06.2026 | 475 dated 22.06.2026 | 8144.06 | 1: 8.07; 2: 6.8; 3: 40; 5: 12; 11: 8.32; 25: 90 |  |  |  | Complying | Complying | 45481.38 | 8.14 | 110 | 384 |  | 182 | [5 empty] | 22.78 | [13 empty] | -
[11 empty] | 01.07.2026 | 555 dt. 09.07.2026 |  | 1: 7.35; 2: 30; 3: 152; 5: 32; 11: 18.21; 25: 600 |  |  |  | Non-Complying | Non-Complying |  | 7.32 | 230 | 720 |  | 404 | [5 empty] | 74.25 | [13 empty] | 1.56X105
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 712 dt. 04.08.2026 |  | 1: 7.35; 2: 17; 3: 88; 5: 28; 6: 538; 7: 45.98; 9: 79.75; 12: 9.33; 13: 4.22; 14: ND; 16: ND; 17: ND; 18: 63.1; 19: 108; 20: 72; 23: 104; 24: 180; 25: 80; 28: 1.72; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: 0.348; 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: 7.5; 55: 979 |  |  |  | Non-Complying | Non-Complying |  | 7.2 | 125 | 432 |  | 208 | 578 | 49.98 |  | 410.12 |  |  | 21.42 | 19.76 | 4.58 |  | 9.6 | ND | 71.6 | 148 | 102 |  |  | 258 | 250 | 1.46X105 |  |  | 2.3 |  |  | BDL(DL=0.001) | BDL(DL=0.230) | 6.482 | 1.7592 | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | 0.732 | BDL(DL=0.001) | [8 empty] | 24 |  |  | 1054
35 | (PKL-STP-015) 1 MLD STP, Ramgarh, Panchkula by ULBD in 30.06.2022
[11 empty] | 01.01.2026 | 4181 dt. 09.01.2026 |  | 1: 7.68; 2: 6.2; 3: 36; 5: 10; 11: ND |  |  |  | Complying | Complying |  | 7.05 | 125 | 408 |  | 145 | [5 empty] | 13.72
[11 empty] | 12.02.2026 | 4512 dated 02.03.2026 |  | 1: 8.42; 2: 7.5; 3: 40; 5: 15; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 8.06 | 120 | 408 |  | 215 | [5 empty] | 14.58 | [13 empty] | -
[11 empty] | 05.03.2026 | 4640 dated 19.03.2026 |  | 1: 8.63; 2: 7.8; 3: 44; 5: 12; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 7.98 | 120 | 396 |  | 176 | [5 empty] | 16.28 | [13 empty] | -
[11 empty] | 16.04.2026 | 129 dated 29.04.2026 |  | 1: 7.1; 2: 6.4; 3: 40; 5: 11; 11: ND; 25: 70 |  |  |  | Complying | Complying |  | 7.94 | 105 | 380 |  | 224 | [5 empty] | 12.59 | [13 empty] | -
[11 empty] | 08.05.2026 | 217 dt. 18.05.2026 | 3566.36 | 1: 8.26; 2: 6.4; 3: 36; 5: 10; 11: ND |  |  |  | Complying | Complying | 2720.54 | 8.1 | 68 | 224 |  | 90 | [5 empty] | 18.36 | [13 empty] | -
[11 empty] | 09.06.2026 | 476 dt. 22.06.2026 | 5886.28 | 1: 8.3; 2: 8.8; 3: 48; 5: 18; 11: 9.86; 25: 90 |  |  |  | Complying | Complying | 5531.5 | 8.14 | 80 | 260 |  | 145 | [5 empty] | 21.84 | [13 empty] | 1.18X 105
[11 empty] | 01.07.2026 | 554 dt. 09.07.2026 | 6066.53 | 1: 7.08; 2: 15.2; 3: 80; 5: 27; 11: 17.4; 25: 200 |  |  |  | Non-Complying | Non-Complying | 76848.533 | 7.88 | 245 | 768 |  | 390 | [5 empty] | 75.65 | [13 empty] | 2.5X 105
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 710 dt. 04.08.2026 |  | 1: 7.3; 2: 6.8; 3: 36; 5: 13; 6: 488; 7: 27.99; 9: 43.04; 12: BDL(DL=0.5); 13: 2.93; 14: ND; 16: ND; 17: ND; 18: 80.6; 19: 106; 20: 72; 23: 128; 24: 178; 25: 90; 28: 2.61; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: BDL(DL=0.264); 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: BDL(DL=02); 55: 889 |  |  |  | Complying | Complying |  | 7.23 | 120 | 404 |  | 176 | 820 | 30.99 |  | 357.89 |  |  | 23.46 | 14.78 | 3.94 |  | 3.6 | ND | 107.5 | 162 | 102 |  |  | 408 | 264 | 1.25X105 |  |  | 2.85 |  |  | 0.408 | BDL(DL=0.230) | 3.428 | 0.9372 | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | BDL(DL=0.5243) | BDL(DL=0.001) | [8 empty] | 23.5 |  |  | 1501
Jind
36 | (JND-STP-001) 15 MLD STP by PHED Jind in Jan, 2009 |  | 20 | 6.5 to 9 | 50 | 20
[11 empty] | 07.01.2026 | 4237 dt. 20.01.2026 |  | 1: 7.48; 2: 7.2; 3: 44; 5: 13; 11: ND |  |  |  | Complying | Complying |  | 7.6 | 145 | 496 |  | 256 | [5 empty] | 13.76
[11 empty] | 11.02.2026 | 4489 dt. 24.02.2026 |  | 1: 7.65; 2: 7.2; 3: 40; 5: 12; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 7.56 | 135 | 472 |  | 288 | [5 empty] | 11.52 | [13 empty] | -
[11 empty] | 18.03.2026 | 4741 dt. 02.04.2026 | 128.652 (m3/h) | 1: 8.76; 2: 7.4; 3: 36; 5: 8; 11: 1.88; 25: 70 |  |  |  | Complying | Complying | 1574.5 (m3/h) | 7.56 | 140 | 480 |  | 224 | [5 empty] | 14.28 | [13 empty] | -
[11 empty] | 16.04.2026 | 132 dt. 29.04.2026 |  | 1: 8.34; 2: 7.5; 3: 48; 5: 8; 11: 2.72; 25: 90 |  |  |  | Complying | Complying |  | 8.32 | 110 | 372 |  | 364 | [5 empty] | 16.72 | [13 empty] | -
[11 empty] | 07.05.2026 | 57-58-A dated 13.05.2026 |  | 1: 7.6; 2: 8.2; 3: 36; 5: 13; 25: 84 |  |  |  | Complying | Complying |  | 8.2 | 72 | 225 |  | 186 | [19 empty] | -
[11 empty] | 18.06.2026 | 348-349- A dt. 23.06.2026 |  | 1: 7.9; 2: 8.4; 3: 40; 5: 14; 25: 76 |  |  |  | Complying | Complying |  | 8.4 | 80 | 256 |  | 218
| July, 2026 1st Phase | [9 empty] | 09.07.2026 | 481-482 A dt. 15.07.2026 |  | 1: 7.8; 2: 7.8; 3: 44; 5: 18; 25: 68 |  |  |  | Complying | Complying |  | 8.2 | 96 | 256 |  | 224 | [19 empty] | 2.4X104
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 565-566-A dt. 04.08.2026 |  | 1: 7.2; 2: 6.8; 3: 44; 5: 8; 6: 420; 7: 123; 8: 109.8; 9: 171; 18: 34; 19: 25.5; 20: 30; 23: 90; 24: 180; 25: 42; 28: 6.5; 29: 2.4; 31: BDL; 52: BDL(DL=4); 55: 1412 |  | 0.9 |  | Complying | Complying |  | 7.8 | 118 | 240 |  | 8 | 914 | 522 | 341.6 | 243.2 | [8 empty] | 145 | 97.2 | 112.2 |  |  | 280 | 680 | 2.4X 10⁴ |  |  | 14.2 | 8 |  | 1.2 | [20 empty] | 42 |  |  | 2832 |  | 2.8
37 | (JND-STP-002) 10 MLD by HUDA Jind in 27.12.2014
[11 empty] | 07.01.2026 | 4246 dt. 20.01.2026 |  | 1: 8.05; 2: 5.8; 3: 32; 5: 11; 11: 2.68 |  |  |  | Complying | Complying |  | 7.87 | 98 | 328 |  | 138 | [5 empty] | 17.28
[11 empty] | 11.02.2026 | 4488 dt. 24.02.2026 | 0.48 | 1: 7.59; 2: 7; 3: 36; 5: 10; 11: ND; 25: 90 |  |  |  | Complying | Complying | - | 7.6 | 145 | 492 |  | 328 | [5 empty] | 17.52 | [13 empty] | -
[11 empty] | 18.03.2026 | 4740 dt. 02.04.2026 |  | 1: 8.01; 2: 5.8; 3: 32; 5: 11; 11: ND; 25: 50 |  |  |  | Complying | Complying |  | 7.76 | 140 | 452 |  | 313 | [5 empty] | 13.22 | [13 empty] | -
[11 empty] | 16.04.2026 | 133 dt. 29.04.2026 |  | 1: 8.34; 2: 6.8; 3: 44; 5: 8; 11: 3.22; 25: 80 |  |  |  | Complying | Complying |  | 8.4 | 125 | 432 |  | 202 | [5 empty] | 12.98 | [13 empty] | -
[11 empty] | 07.05.2026 | 55-56-A dated 13.05.2026 |  | 1: 7.2; 2: 7.6; 3: 32; 5: 14; 25: 72 |  |  |  | Complying | Complying |  | 8.6 | 76 | 248 |  | 216 | [19 empty] | -
[11 empty] | 18.06.2026 | 346-347- A dt. 23.06.2026 | 38910.65 | 1: 7.8; 2: 7.4; 3: 40; 5: 12; 25: 56 |  |  |  | Complying | Complying | - | 8.2 | 105 | 280 |  | 218 | [19 empty] | 9.6 X 10⁴
| July, 2026 1st Phase | [9 empty] | 09.07.2026 | 485-486 A dt. 15.07.2026 |  | 1: 7.4; 2: 8.4; 3: 44; 5: 12; 25: 32 |  |  |  | Complying | Complying |  | 8.8 | 108 | 272 |  | 240 | [19 empty] | 6.4X 10⁴ | [26 empty] | 14
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 569-570-A dt. 04.08.2026 |  | 1: 7.5; 2: 7.2; 3: 36; 5: 12; 6: 356; 7: 158.1; 8: 61; 9: 125.6; 18: 32; 19: 21.9; 20: 22; 23: 50; 24: 145; 25: 80; 28: 6.8; 29: 1.7; 31: BDL; 52: BDL(DL=4); 55: 1120 |  | 0.8 |  | Complying | Complying |  | 8.4 | 96 | 232 |  | 156 | 816 | 522 | 292.8 | 392.1 | [8 empty] | 112 | 131.2 | 168.3 |  |  | 240 | 960 | 5.6X 10⁴ |  |  | 6.8 | 1.7 |  | 1.5 | [20 empty] | 36 |  |  | 2516 |  | 2.3
[11 empty] | 04.08.2026 | 659-660-A dt. 11.08.2026 |  | 1: 7.9; 2: 7.4; 3: 42; 5: 18; 6: 649; 7: 210.82; 8: 280.6; 9: 117.2; 18: 140; 19: 70.5; 20: 88.18; 23: 230; 24: 510; 25: 56; 28: 15.72; 29: 6; 31: 0.9; 52: BDL(DL=4); 55: 2180 |  |  |  | Complying | Complying |  | 8.2 | 98 | 160 |  | 168 | 980 | 381.49 | 634.4 | 381.7 | [8 empty] | 248 | 165.2 | 248.5 |  |  | 520 | 1300 | 3.6X 10⁴ |  |  | 17.24 | 11.6 |  | 2.2 | [20 empty] | 28 |  |  | 2956 |  | 4.2
38 | (JND-STP-003) (3.5 MLD) 5 MLD Patiala Road , Narwana by PHED in Jan , 2011 |  | 30 | 7 to 8 | 250 | 50
[11 empty] | 12.01.2026 | 4302 dt. 21.01.2026 |  | 1: 7.06; 2: 5.6; 3: 36; 5: 9; 11: ND |  |  |  | Complying | Complying |  | 7.64 | 140 | 508 |  | 225 | [5 empty] | 16.72
[11 empty] | 24.02.2026 | 4580 dated 10.03.2026 | 72.5 | 1: 8.09; 2: 7.6; 3: 40; 5: 9; 11: ND; 25: ND |  |  |  | Complying | Complying |  | 7.4 | 108 | 368 |  | 138 | [19 empty] | -
[11 empty] | 18.03.2026 | 4735 dt. 02.04.2026 | 72.5 | 1: 8.6; 2: 3.6; 3: 24; 5: 8; 11: ND; 25: ND |  |  |  | Complying | Complying | 75.5 | 7.99 | 120 | 396 |  | 235 | [5 empty] | 14.89 | [13 empty] | -
[11 empty] | 16.04.2026 | 141 dt. 29.04.2026 | 42.4 | 1: 7.8; 2: 8.5; 3: 48; 5: 9; 11: ND; 25: 42.4 |  |  |  | Complying | Complying | 40.6 | 8.63 | 125 | 408 |  | 240 | [5 empty] | 13.25 | [13 empty] | -
[11 empty] | 14.05.2026 | 123-124-A |  | 1: 7.2; 2: 15; 3: 48; 5: 16; 11: ND; 25: 150 |  |  |  | Non complying | Non complying |  | 8.4 | 132 | 424 |  | 256 | [19 empty] | -
[11 empty] | 19.06.2026 | 356-357- A dt. 24.06.2026 | Not working | 1: 7.5; 2: 12; 3: 56; 5: 18; 25: 180 |  |  |  | Non complying | Non complying |  | 8.6 | 110 | 456 |  | 224 | [19 empty] | 6.4 X 10⁴
| July, 2026 1st Phase | [9 empty] | 08.07.2026 | 469-470 dt. 14.07.2026 |  | 1: 7.8; 2: 9.4; 3: 48; 5: 16; 25: 96 |  |  |  | Complying | Complying |  | 8.2 | 102 | 432 |  | 248 | [19 empty] | 5.2 X 10⁴
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 555-556-A dt. 04.08.2026 |  | 1: 7.2; 2: 7.8; 3: 36; 5: 11; 6: 372; 7: 128; 8: 152.5; 9: 140.2; 18: 32; 19: 34; 20: 22; 23: 125; 24: 195; 25: 72; 28: 6; 29: 4.2; 31: 0.8; 52: BDL(DL=4); 55: 970 |  | 0.2 |  | Complying | Complying |  | 8.7 | 118 | 288 |  | 165 | 1026 | 532.1 | 152.5 | 140.2 | [8 empty] | 32 | 34 | 22 |  |  | 125 | 195 | 5.6X 10⁴ |  |  | 6 | 4.2 |  | 0.8 | [20 empty] | 42 |  |  | 2982 |  | 1.7
39 | (JND-STP-011) (3.75 MLD) 7 MLD STP, Dharodi Road, Narwana Jind by PHED in Jan , 2011 |  | 30 | 7 to 8 | 250 | 50
[11 empty] | 12.01.2026 | 4303 dt. 21.01.2026 |  | 1: 7.79; 2: 7; 3: 44; 5: 13; 11: ND |  |  |  | Complying | Complying |  | 7.59 | 130 | 472 |  | 265 | [5 empty] | 18.36
[11 empty] | 24.02.2026 | 4581 dated 10.03.2026 |  | 1: 8.3; 2: 7; 3: 36; 5: 13; 11: ND |  |  |  | Complying | Complying |  | 7.28 | 125 | 420 |  | 118 | [19 empty] | -
[11 empty] | 18.03.2026 | 4733 dt. 02.04.2026 |  | 1: 7.68; 2: 7.8; 3: 44; 5: 15; 11: 3.74; 25: 90 |  |  |  | Complying | Complying |  | 7.9 | 150 | 496 |  | 212 | [5 empty] | 15.62 | [13 empty] | -
[11 empty] | 16.04.2026 | 142 dt. 29.04.2026 | 8.4 | 1: 7.5; 2: 8.2; 3: 44; 5: 18; 11: ND; 25: 70 |  |  |  | Complying | Complying | - | 8.29 | 150 | 528 |  | 348 | [5 empty] | 14.29 | [13 empty] | -
[11 empty] | 14.05.2026 | 125-126-A dated 20.05.2026 |  | 1: 8.2; 2: 14; 3: 42; 5: 19; 11: ND; 25: 210 |  |  |  | Non complying | Non complying |  | 8.6 | 148 | 548 |  | 364 | [19 empty] | -
[11 empty] | 19.06.2026 | 352-353- A dt. 24.06.2026 | Not working | 1: 8; 2: 9.2; 3: 32; 5: 18; 25: 72 |  |  |  | Complying | Complying |  | 8.4 | 168 | 536 |  | 348 | [19 empty] | 1.2 X 105
| July, 2026 1st Phase | [9 empty] | 08.07.2026 | 473-474 A dt. 14.07.2026 |  | 1: 7.8; 2: 8.8; 3: 36; 5: 17; 25: 72 |  |  |  | Complying | Complying |  | 8.8 | 160 | 464 |  | 320 | [19 empty] | 4.2 X 104
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 561-562-A dt. 04.08.2026 |  | 1: 7.6; 2: 7.4; 3: 40; 5: 15; 6: 256; 7: 102.9; 8: 128.1; 9: 87.2; 18: 39; 19: 25.5; 20: 32; 23: 105; 24: 185; 25: 76; 28: 7.3; 29: 2.6; 31: 0.6; 52: BDL(DL=4); 55: 782 |  | 0.6 |  | Complying | Complying |  | 8.5 | 110 | 256 |  | 196 | 948 | 562.2 | 353.8 | 275.5 | [8 empty] | 139 | 87.5 | 128.2 |  |  | 290 | 680 | 2.8X 10⁴ |  |  | 13.4 | 6.6 |  | 1.8 | [20 empty] | 40 |  |  | 2856 |  | 1.8
40 | (JND-STP-005) 02 MLD STP, PHED , Dablain Road, Narwana, Jind (24.5.2017) |  | 20 | 7 to 8.50 | 100 | 40
[11 empty] | 12.01.2026 | 4301 dt. 21.01.2026 | 51.1 | 1: 7.15; 2: 7.2; 3: 48; 5: 12; 11: ND |  |  |  | Complying | Complying | - | 8.56 | 125 | 420 |  | 255 | [5 empty] | 13.84
[11 empty] | 24.02.2026 | 4579 dated 10.03.2026 |  | 1: 8.09; 2: 7.2; 3: 48; 5: 15; 11: ND |  |  |  | Complying | Complying | - | 7.22 | 120 | 392 |  | 182
[11 empty] | 18.03.2026 | 4734 dt. 02.04.2026 | 76.5 | 1: 7.93; 2: 9; 3: 48; 5: 14; 11: ND; 25: 90 |  |  |  | Complying | Complying | - | 7.9 | 155 | 484 |  | 244 | [5 empty] | 14.98 | [13 empty] | -
[11 empty] | 16.04.2026 | 139 dt. 29.04.2026 |  | 1: 7.64; 2: 6.8; 3: 40; 5: 11; 11: 1.86; 25: 80 |  |  |  | Complying | Complying |  | 8.26 | 105 | 380 |  | 285 | [5 empty] | 15.28 | [13 empty] | -
[11 empty] | 14.05.2026 | 117-118-A dated 20.05.2026 |  | 1: 7.7; 2: 8.8; 3: 42; 5: 15; 11: ND; 25: 88 |  |  |  | Complying | Complying |  | 8.4 | 102 | 348 |  | 292
[11 empty] | 19.06.2026 | 354-355- A dt. 24.06.2026 | 0.8 | 1: 7.8; 2: 8.6; 3: 40; 5: 14; 25: 80 |  |  |  | Complying | Complying | 2.2 | 8.6 | 96 | 372 |  | 280 | [19 empty] | 7.2 X 10⁴
| July, 2026 1st Phase | [9 empty] | 08.07.2026 | 471-472 A dt. 14.07.2026 |  | 1: 7.4; 2: 8.2; 3: 44; 5: 12; 25: 56 |  |  |  | Complying | Complying |  | 8.4 | 92 | 360 |  | 256 | [19 empty] | 1.8 X 10⁴
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 559-560-A dt. 04.08.2026 |  | 1: 7.5; 2: 8.2; 3: 44; 5: 14; 6: 395; 7: 70; 8: 170.8; 9: 95.2; 18: 48; 19: 27.9; 20: 38; 23: 140; 24: 210; 25: 80; 28: 8.4; 29: 3.2; 31: 0.7; 52: BDL(DL=4); 55: 1050 |  | 0.5 |  | Complying | Complying |  | 8.9 | 106 | 262 |  | 202 | 872 | 522 | 317.2 | 328.7 | [8 empty] | 124 | 92.3 | 112.2 |  |  | 260 | 660 | 4.2X 10⁴ |  |  | 12.3 | 7.2 |  | 1.2 | [20 empty] | 42 |  |  | 2982 |  | 1.7
41 | (JND-STP-006) 3 MLD STP Uchana Jind by PHED in 30.06.2022 |  | 20 | 7.0 to 8 | 250 | 40
[11 empty] | 21.01.2026 | 4345 dt. 03.02.2026 |  | 1: 7.89; 2: 5.2; 3: 36; 5: 16; 11: 1.22 |  |  |  | Complying | Complying |  | 7.09 | 120 | 416 |  | 388 | [5 empty] | 15.76
[11 empty] | 25.02.2026 | 4584 dt. 10.03.2026 |  | 1: 7.78; 2: 7.2; 3: 44; 5: 10; 11: ND; 25: 60 |  |  |  | Complying | Complying |  | 7.18 | 125 | 428 |  | 155 | [5 empty] | 14.28 | [13 empty] | -
[11 empty] | 19.03.2026 | 4767 dated 03.04.2026 | 58.4 | 1: 8.63; 2: 7.8; 3: 36; 5: 12; 11: ND; 25: 90 |  |  |  | Complying | Complying | 75.01 | 7.99 | 175 | 608 |  | 372 | [5 empty] | 15.22
[11 empty] | 23.04.2026 | 5-6-A dated 28.04.2026 | 80.7 | 1: 6.9; 2: 8; 3: 40; 5: 14; 11: ND; 25: 70 |  |  |  | Complying | Complying | 89.5 | 7.2 | 172 | 576 |  | 348
[11 empty] | 07.05.2026 | 69-70-A dated 13.05.2026 | 80.43 | 1: 6.8; 2: 7.1; 3: 40; 5: 11; 11: ND; 25: 52 |  |  |  | Complying | Complying | 95.83 | 7.2 | 116 | 448 |  | 226
[11 empty] | 19.06.2026 | 362-363- A dt. 24.06.2026 | 425234.62 | 1: 7.8; 2: 9.8; 3: 56; 5: 13; 25: 80 |  |  |  | Complying | Complying | 195.8 | 8.6 | 164 | 568 |  | 364 | [19 empty] | 4.8 X104
| July, 2026 1st Phase | [9 empty] | 01.07.2026 | 384-385- A dt. 07.07.2026 | 102.98 | 1: 7.6; 2: 8.8; 3: 36; 5: 14; 25: 56 |  |  |  | Complying | Complying | 104.17 | 7.9 | 176 | 272 |  | 186 | [19 empty] | 4.8 X104
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 547-548-A dt. 04.08.2026 | 91.89 | 1: 7.4; 2: 6.9; 3: 32; 5: 12; 6: 420; 7: 110.4; 8: 91.5; 9: 17.3; 18: 48; 19: 19.4; 20: 24.1; 23: 75; 24: 140; 25: 26; 28: 10.2; 29: 19; 31: BDL; 52: BDL(DL=4); 55: 996 |  | 0.8 |  | Complying | Complying | 95.83 | 8.4 | 118 | 148 |  | 222 | 815 | 491.9 | 512.4 | 126.2 | [8 empty] | 158 | 116.6 | 144.3 |  |  | 420 | 840 | 4.8 X104 |  |  | 13.8 | 10.8 |  | 2.1 | [20 empty] | 26 |  |  | 2470 |  | 2.1
42 | (JND-STP-007) 1.5 MLD Uchana by PHED in 31.5.2013 |  | 20 | 7 to 8.50 | 250 | 40
[11 empty] | 21.01.2026 | 4346 dt. 03.02.2026 | 58.7 | 1: 7.45; 2: 8.4; 3: 48; 5: 19; 11: ND |  |  |  | Complying | Complying | - | 6.96 | 125 | 420 |  | 296 | [5 empty] | 14.28
[11 empty] | 25.02.2026 | 4585 dt. 10.03.2026 |  | 1: 7.78; 2: 6; 3: 32; 5: 14; 11: ND; 25: 70 |  |  |  | Complying | Complying |  | 7.18 | 125 | 416 |  | 182 | [5 empty] | 15.36 | [13 empty] | -
[11 empty] | 19.03.2026 | 4768 dated 03.04.2026 | 45.92 | 1: 8.17; 2: 28; 3: 148; 5: 68; 11: ND; 25: 600 |  |  |  | Non complying | Non complying | 52.09 | 7.84 | 120 | 408 |  | 188 | [5 empty] | 19.75
[11 empty] | 23.04.2026 | 3-4-A dated 28.04.2026 | 46.8 | 1: 6.9; 2: 14; 3: 48; 5: 26; 11: ND; 25: 300 |  |  |  | Non complying | Non complying | 54.5 | 7.3 | 138 | 456 |  | 208
[11 empty] | 07.05.2026 | 67-68-A dated 13.05.2026 | 44.3 | 1: 7.4; 2: 8.9; 3: 44; 5: 16; 11: ND; 25: 76 |  |  |  | Complying | Complying | 54.2 | 7.6 | 105 | 356 |  | 224
[11 empty] | 19.06.2026 | 360-361- A dt. 24.06.2026 | Not working | 1: 7.4; 2: 28; 3: 142; 5: 19; 25: 560 |  |  |  | Non complying | Non complying |  | 7.8 | 128 | 424 |  | 182 | [19 empty] | 4.2 X10⁴
| July, 2026 1st Phase | [9 empty] | 01.07.2026 | 382-383- A dt. 07.07.2026 | 48.4 | 1: 8.1; 2: 8.2; 3: 40; 5: 18; 25: 72 |  |  |  | Complying | Complying | 49.58 | 9.1 | 96 | 224 |  | 196 | [19 empty] | 2.4 X10⁴
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 549-550-A dt. 04.08.2026 | 55.44 | 1: 7.2; 2: 8.2; 3: 24; 5: 14; 6: 356; 7: 75.2; 8: 97.6; 9: 18.6; 18: 24; 19: 12.2; 20: 12; 23: 80; 24: 80; 25: 56; 28: 6.9; 29: 2; 31: BDL; 52: BDL(DL=4); 55: 820 |  | 0.7 |  | Complying | Complying | 59.17 | 8.6 | 102 | 280 |  | 148 | 790 | 391.5 | 500.2 | 141.5 | [8 empty] | 142 | 131.2 | 168.3 |  |  | 410 | 960 | 3.6X 10⁴ |  |  | 11.6 | 10.6 |  | 2.4 | [20 empty] | 24 |  |  | 2278 |  | 2.4
43 | (JND-STP-008) 5 MLD STP Jind by PHED in 1.4.2016 |  | 20 | 7 to 8.50 | 250 | 40
[11 empty] | 07.01.2026 | 4241 dt. 20.01.2026 | 164.7 | 1: 7.46; 2: 5.2; 3: 40; 5: 12; 11: ND |  |  |  | Complying | Complying | 168.5 | 6.96 | 110 | 396 |  | 208 | [5 empty] | 13.58
[11 empty] | 11.02.2026 | 4485 dt. 24.02.2026 |  | 1: 7.12; 2: 50; 3: 212; 5: 96; 11: 12.32; 25: 1200 |  |  |  | Non Complying | Non Complying |  | 7.29 | 112 | 396 |  | 178 | [5 empty] | 19.72 | [13 empty] | -
[11 empty] | 18.03.2026 | 4743 dt. 02.04.2026 |  | 1: 8; 2: 7.2; 3: 40; 5: 13; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 8.01 | 140 | 492 |  | 293 | [5 empty] | 11.89 | [13 empty] | -
[11 empty] | 16.04.2026 | 134 dt. 29.04.2026 |  | 1: 7.1; 2: 7.8; 3: 48; 5: 14; 11: ND; 25: 70 |  |  |  | Complying | Complying |  | 8.47 | 102 | 328 |  | 236 | [5 empty] | 15.84 | [13 empty] | -
[11 empty] | 07.05.2026 | 59-60-A dated 13.05.2026 | 95.2 | 1: 7.2; 2: 8.1; 3: 34; 5: 15; 11: ND; 25: 52 |  |  |  | Complying | Complying | 59.7 | 7.8 | 92 | 384 |  | 236
[11 empty] | 18.06.2026 | 342-343- A dt. 23.06.2026 | 43.3 | 1: 7.4; 2: 8.4; 3: 40; 5: 16; 25: 48 |  |  |  | Complying | Complying |  | 8 | 86 | 368 |  | 224 | [19 empty] | 8.2 X10⁴
| July, 2026 1st Phase | [9 empty] | 09.07.2026 | 477-478 A dt. 14.07.2026 |  | 1: 7.9; 2: 38; 3: 96; 5: 28; 25: 1.2X103 |  |  |  | Non Complying | Non Complying |  | 8.9 | 102 | 384 |  | 264 | [19 empty] | 5.6 X10⁴
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 551-552-A dt. 04.08.2026 |  | 1: 7.5; 2: 7.6; 3: 28; 5: 9; 6: 452; 7: 95.3; 8: 91.5; 9: 42.2; 18: 32; 19: 24.3; 20: 32.1; 23: 75; 24: 180; 25: 72; 28: 6; 29: 1.9; 31: 0.9; 52: BDL(DL=4); 55: 1220 |  | 0.6 |  | Complying | Complying |  | 8.6 | 106 | 248 |  | 224 | 958 | 411.2 | 305 | 272.6 | [8 empty] | 32 | 145.2 | 132.3 |  |  | 250 | 980 | 2.8X 10⁴ |  |  | 12.9 | 9.4 |  | 2.6 | [20 empty] | 28 |  |  | 2910 |  | 2.1
[11 empty] | 04.08.2026 | 657-658-A dt. 11.08.2026 |  | 1: 7.8; 2: 12; 3: 56; 5: 22; 6: 719; 7: 205.8; 8: 317.2; 9: 162.8; 18: 102; 19: 55.9; 20: 72.14; 23: 260; 24: 410; 25: 180; 28: 12.75; 29: 6.2; 31: 1.2; 52: BDL(DL=4); 55: 2156 |  | 1.2 |  | Non Complying | Non Complying |  | 8.8 | 96 | 148 |  | 156 | 822 | 451.76 | 658.8 | 251.6 | [8 empty] | 324 | 170.1 | 216.43 |  |  | 540 | 1240 | 2.5X 10⁴ |  |  | 23.31 | 14 |  | 2.4 | [20 empty] | 24 |  |  | 2466 |  | 5.2
44 | (JND-STP-009) 7 MLD STP, Jind by PHED in 30.11.2019 |  | 10 | 6.5 to 9 | 50 | 20
[11 empty] | 07.01.2026 | 4238 dt. 20.01.2026 |  | 1: 7.79; 2: 7.2; 3: 44; 5: 12; 11: ND |  |  |  | Complying | Complying |  | 7.56 | 150 | 508 |  | 245 | [5 empty] | 12.89
[11 empty] | 11.02.2026 | 4486 dt. 24.02.2026 |  | 1: 8.2; 2: 5.2; 3: 36; 5: 8; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 7.46 | 240 | 840 |  | 510 | [5 empty] | 16.93 | [13 empty] | -
[11 empty] | 18.03.2026 | 4742 dt. 02.04.2026 |  | 1: 8.89; 2: 8.2; 3: 44; 5: 11; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 7.48 | 135 | 476 |  | 185 | [5 empty] | 13.26 | [13 empty] | -
[11 empty] | 16.04.2026 | 136 dt. 29.04.2026 | 2.253 (m3/h) | 1: 8.1; 2: 5.8; 3: 40; 5: 8; 11: ND; 25: 60 |  |  |  | Complying | Complying |  | 8.13 | 108 | 352 |  | 370 | [5 empty] | 15.35 | [13 empty] | -
[11 empty] | 07.05.2026 | 63-64-A dated 13.05.2026 | 43.74 | 1: 7.2; 2: 7.8; 3: 30; 5: 14; 11: ND; 25: 56 |  |  |  | Complying | Complying | 5790.4 | 7.8 | 78 | 292 |  | 182
[11 empty] | 18.06.2026 | 344-345- A dt. 23.06.2026 | 212.011 | 1: 7.4; 2: 8.4; 3: 44; 5: 16; 25: 62 |  |  |  | Complying | Complying | 1299425 | 8.5 | 76 | 282 |  | 148 | [19 empty] | 8.2 X 10⁴
| July, 2026 1st Phase | [9 empty] | 09.07.2026 | 489-490 A dt. 14.07.2026 |  | 1: 7.4; 2: 7.2; 3: 40; 5: 8; 25: 90; 52: BDL |  |  |  | Complying | Complying |  | 8.6 | 88 | 288 |  | 186 | [19 empty] | 2.4 X 10⁴ | [26 empty] | 18
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 567-568-A dt. 04.08.2026 |  | 1: 7.3; 2: 6.4; 3: 40; 5: 10; 6: 316; 7: 128; 8: 115.9; 9: 145; 18: 29; 19: 25.5; 20: 28.1; 23: 95; 24: 175; 25: 86; 28: 5.6; 29: 2.6; 31: BDL; 52: BDL(DL=4); 55: 1260 |  | 0.7 |  | Complying | Complying |  | 8 | 105 | 224 |  | 112 | 820 | 582.2 | 305 | 386.1 | [8 empty] | 124 | 126.4 | 200.4 |  |  | 250 | 1020 | 3.2X 10⁴ |  |  | 9.7 | 5.4 |  | 1.8 | [20 empty] | 32 |  |  | 2418 |  | 2.1
[11 empty] | 04.08.2026 | 653-654-A dt. 11.08.2026 |  | 1: 7.9; 2: 14; 3: 48; 5: 22; 6: 643; 7: 190.74; 8: 292.8; 9: 172.8; 18: 112; 19: 55.9; 20: 72.14; 23: 240; 24: 410; 25: 120; 28: 14; 29: 5.8; 31: 1.1; 52: BDL(DL=4); 55: 1928 |  | 1.4 |  | Non Complying | Non Complying |  | 8.2 | 96 | 128 |  | 128 | 820 | 491.92 | 610 | 351.7 | [8 empty] | 245 | 145.8 | 184.37 |  |  | 500 | 1060 | 3.6X 10⁴ |  |  | 19.07 | 12.8 |  | 2.4 | [20 empty] | 24 |  |  | 2466 |  | 5.2
45 | (JND-STP-010) 9 MLD STP Safidon, Jind by PHED in 31.05.2018 |  | 10 | 5.5 to 9 | 100 | 10
[11 empty] | 21.01.2026 | 4347 dt. 03.02.2026 | 37.5 | 1: 7.27; 2: 7.2; 3: 44; 5: 17; 11: ND |  |  |  | Complying | Complying | 762.4 | 7 | 130 | 428 |  | 258 | [5 empty] | 13.28
[11 empty] | 25.02.2026 | 4583 dt. 10.03.2026 |  | 1: 8.09; 2: 6.4; 3: 32; 5: 13; 11: ND; 25: 50 |  |  |  | Complying | Complying |  | 7.56 | 102 | 380 |  | 158 | [5 empty] | 12.66 | [13 empty] | -
[11 empty] | 18.03.2026 | 4737 dt. 02.04.2026 | 42.4 | 1: 8.3; 2: 6.8; 3: 36; 5: 11; 11: ND; 25: 70 |  |  |  | Complying | Complying | 18.3 | 7.9 | 120 | 404 |  | 162 | [5 empty] | 14.98 | [13 empty] | -
[11 empty] | 16.04.2026 | 138 dt. 29.04.2026 | 648.1 | 1: 7.59; 2: 7.8; 3: 48; 5: 13; 11: ND; 25: 90 |  |  |  | Complying | Complying | 79.377 | 8.29 | 210 | 728 |  | 542 | [5 empty] | 18.72 | [13 empty] | -
[11 empty] | 07.05.2026 | 71-72-A dated 13.05.2026 | 248.79 | 1: 7.5; 2: 7.4; 3: 44; 5: 15; 11: ND; 25: 86 |  |  |  | Complying | Complying | 312.5 | 8.1 | 168 | 696 |  | 412
[11 empty] | 18.06.2026 | 338-339- A dt. 23.06.2026 | 748.7 | 1: 7.8; 2: 6.8; 3: 40; 5: 18; 25: 72 |  |  |  | Complying | Complying | 79.29 | 8.1 | 142 | 568 |  | 396 | [19 empty] | 1.1 X 10⁴
| July, 2026 1st Phase | [9 empty] | 09.07.2026 | 487-488 A dt. 15.07.2026 | 103.26 | 1: 7.6; 2: 8; 3: 36; 5: 17; 25: 72 |  |  |  | Complying | Complying | 555.8 | 9.2 | 110 | 248 |  | 296 | [19 empty] | 5.6 X 10⁴
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 545-546-A dt. 04.08.2026 | 276.7 | 1: 8; 2: 42; 3: 136; 5: 38; 6: 619; 7: 261; 8: 286.7; 9: 74.2; 18: 110; 19: 97.2; 20: 120.2; 23: 235; 24: 700; 25: 4.8X103; 28: 10.5; 29: 6.7; 31: 0.9; 52: BDL(DL=4); 55: 2190 |  | 0.9 |  | Non-Complying | Non-Complying | 852.4 | 8.4 | 110 | 408 |  | 192 | 1150 | 451.7 | 585.6 | 138.2 | [8 empty] | 172 | 189.5 | 256.6 |  |  | 480 | 1420 | 2.2 X104 |  |  | 11.5 | 12.4 |  | 4.2 | [20 empty] | 21 |  |  | 2820 |  | 2.8
Kaithal
46 | (KTL-STP-001) 10 MLD STP Cheeka , Kaithal by PHED in 1.4.2013 |  | 10 | 6.5 to 9 | 50 | 20
[11 empty] | 01.01.2026 | 4176 dt. 09.01.2026 |  | 1: 7.47; 2: 7.2; 3: 36; 5: 11; 11: ND |  |  |  | Complying | Complying |  | 7.05 | 160 | 540 |  | 380 | [5 empty] | 15.63
[11 empty] | 08.04.2026 | 63 dt. 23.04.2026 | NA | 1: 7.67; 2: 6.6; 3: 36; 5: 15; 11: ND |  |  |  | Complying | Complying | 604.8 | 7.2 | 165 | 540 |  | 295 | [5 empty] | 13.72 | [13 empty] | -
[11 empty] | 11.05.2026 | HRL/WW-II/2026/47-48 |  | 1: 7.5; 2: 26; 3: 106; 5: 62 |  |  |  | Non-Complying | Non-Complying |  | 7.1 | 128 | 366 |  | 284
[11 empty] | 04.06.2026 | HRL/WW-II/2026/108-109 A dt. 10.06.2026 |  | 1: 7.2; 2: 6; 3: 24; 5: 12 |  |  |  | Complying | Complying |  | 7.8 | 108 | 304 |  | 278
| July, 2026 1st Phase | [9 empty] | 03.07.2026 | HRL/WW-II/2026/167-168 A dt. 08.07.2026 |  | 1: 7.9; 2: 5; 3: 20; 5: 10; 25: 78; 52: BDL |  |  |  | Complying | Complying |  | 7.7 | 88 | 296 |  | 216 | [19 empty] | 3.1 X 10⁴ | [26 empty] | 16.8
| July, 2026 2nd Phase | [9 empty] | 16.07.2026 | HRL/WW-II/2026/179-180 A dt. 28.07.2026 |  | 1: 7.4; 2: 25; 3: 92; 5: 78; 6: 896; 7: 179.9; 8: 561; 9: 55; 18: 240; 19: 24.3; 20: 80; 23: 460; 24: 180; 25: 1.8X103; 28: 7.8; 29: 5.6; 31: 0.5; 52: BDL(DL=4); 55: 1370 |  | 3.5 |  | Non-Complying | Non-Complying |  | 7.1 | 117 | 464 |  | 286 | 992 | 249.9 | 561 | 78 | [8 empty] | 240 | 38.9 | 40 |  |  |  | 200 | 3.1X104 |  |  | 7.8 | 6.4 |  | 0.8 | [20 empty] | 1 |  |  | 1517 |  | 8.5
[11 empty] | 06.08.2026 | HRL/WW-II/2026/285 dt.18.08.2026 | 601.13 | 1: 7.6; 2: 29; 3: 96; 5: 108; 6: 902; 7: 184.9; 8: 829.6; 9: 98; 18: 106.5; 19: 19.4; 20: 40; 23: 680; 24: 180; 25: 2.4X104; 28: 3.5; 29: 10; 31: 0.9; 52: 8.4; 55: 1384 |  | 3.9 |  | Non-Complying | Non-Complying
47 | (KTL-STP-002) 10 MLD STP, Jind Road Kaithal by PHED in September, 2012 |  | 10 | 7 to 8.50 | 100 | 20
[11 empty] | 30.01.2026 | 4395 dt. 09.02.2026 | 8.2 | 1: 8.25; 2: 6.8; 3: 40; 5: 13; 11: ND |  |  |  | Complying | Complying | 13.4 | 6.8 | 140 | 448 |  | 238 | [5 empty] | 13.28
[11 empty] | 18.02.2026 | 4547 dt. 03.03.2026 |  | 1: 7.99; 2: 7; 3: 36; 5: 13; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 7.3 | 130 | 452 |  | 255 | [5 empty] | 13.78 | [13 empty] | -
[11 empty] | 18.03.2026 | 4750 dt. 02.04.2026 | - | 1: 7.34; 2: 6.6; 3: 44; 5: 15; 11: ND; 25: 70 |  |  |  | Complying | Complying | 476.9 | 7.6 | 130 | 436 |  | 194 | [5 empty] | 13.76 | [13 empty] | -
[11 empty] | 08.04.2026 | 61 dt. 23.04.2026 |  | 1: 7; 2: 6.8; 3: 44; 5: 16; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 6.92 | 122 | 424 |  | 169 | [5 empty] | 17.36 | [13 empty] | -
[11 empty] | 11.05.2026 | HRL/WW-II/2026/43-44 | - | 1: 7.6; 2: 7; 3: 40; 5: 14 |  |  |  | Complying | Complying | 5.58 | 7.5 | 104 | 328 |  | 226
[11 empty] | 04.06.2026 | HRL/WW-II/2026/114-115 A 10.06.2026 |  | 1: 8.2; 2: 7; 3: 36; 5: 15 |  |  |  | Complying | Complying
| July, 2026 2nd Phase | [9 empty] | 16.07.2026 | HRL/WW-II/2026/193-194 A dt. 28.07.2026 |  | 1: 7.4; 2: 7; 3: 44; 5: 10; 6: 968; 7: 209.9; 8: 500; 9: 125; 18: 54; 19: 53; 20: 68; 23: 410; 24: 250; 25: 90; 28: 1.5; 29: 3.2; 31: 0.3; 52: BDL(DL=4); 55: 1480 |  | 0.9 |  | Complying | Complying |  | 7.1 | 72 | 296 |  | 178 | 2330 | 249.8 | 646 | 255 | [8 empty] | 148 | 53 | 68 |  |  |  | 390 | 3.5X104 |  |  | 3.3 | 1.6 |  | 0.9 | [20 empty] | 8 |  |  | 3582 |  | 3.6
[11 empty] | 04.08.2026 | HRL/WW-II/2026/259-260 A dt.11.08.2026 | 601.13 | 1: 7.8; 2: 7; 3: 28; 5: 10; 6: 582; 7: 99.9; 8: 451; 9: 120; 18: 50; 19: 29; 20: 36; 23: 370; 24: 210; 25: 76; 28: 1.5; 29: 3.2; 31: 1.2; 52: BDL(DL=4); 55: 893 |  | 0.8 |  | Complying | Complying |  | 7.2 | 83 | 276 |  | 186 | 1140 | 254.9 | 586 | 248 | [8 empty] | 146 | 51 | 64 |  |  |  | 370 | 3.8X 10⁴ |  |  | 3.3 | 2.2 |  | 1.1 | [20 empty] | 14.8 |  |  | 1752 |  | 3.2
48 | (KTL-STP-003) 10 MLD STP Manas Road, Kaithal by PHED in June , 2006 (MBBR+TT) |  | 10 | 6.5 to 9 | 50 | 20
[11 empty] | 29.01.2026 | 4394 dt. 09.02.2026 | 340.9 | 1: 8.12; 2: 6.4; 3: 36; 5: 12; 11: ND |  |  |  | Complying | Complying | - | 7.12 | 125 | 420 |  | 179 | [5 empty] | 15.72
[11 empty] | 18.02.2026 | 4545 dt. 03.03.2026 |  | 1: 8.32; 2: 7.8; 3: 48; 5: 12; 11: 1.88; 25: 90 |  |  |  | Complying | Complying |  | 7.44 | 102 | 348 |  | 248 | [5 empty] | 15.28 | [13 empty] | -
[11 empty] | 18.03.2026 | 4752 dt. 02.04.2026 |  | 1: 7.22; 2: 7.6; 3: 48; 5: 16; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 7.35 | 130 | 424 |  | 208 | [5 empty] | 14.72 | [13 empty] | -
[11 empty] | 08.04.2026 | 62 dt. 23.04.2026 |  | 1: 7.37; 2: 5.6; 3: 28; 5: 9; 11: ND; 25: 70 |  |  |  | Complying | Complying |  | 7.34 | 145 | 488 |  | 252 | [5 empty] | 14.78 | [13 empty] | -
[11 empty] | 11.05.2026 | HRL/WW-II/2026/45-46 |  | 1: 7.6; 2: 6; 3: 32; 5: 13 |  |  |  | Complying | Complying |  | 7.7 | 112 | 344 |  | 216
[11 empty] | 10.06.2026 | HRL/WW-II/2026/112-113 A |  | 1: 8; 2: 7; 3: 42; 5: 14 |  |  |  | Complying | Complying |  | 7.8 | 114 | 328 |  | 220
| July, 2026 1st Phase | [9 empty] | 03.07.2026 | HRL/WW-II/2026/165-166 A 08.07.2026 | 340.9 | 1: 8; 2: 6; 3: 24; 5: 16; 25: 80; 52: BDL |  |  |  | Complying | Complying | - | 7.7 | 108 | 304 |  | 246 | [19 empty] | 3.1 X 10⁴ | [26 empty] | 22
| July, 2026 2nd Phase | [9 empty] | 16.07.2026 | HRL/WW-II/2026/191-192 A dt. 28.07.2026 |  | 1: 7.4; 2: 8; 3: 48; 5: 14; 6: 970; 7: 224.9; 8: 451; 9: 130; 18: 58; 19: 41; 20: 290; 23: 370; 24: 290; 25: 96; 28: 1.7; 29: 1; 31: 0.2; 52: BDL(DL=4); 55: 1492 |  | 1 |  | Complying | Complying |  | 7.1 | 76 | 304 |  | 198 | 2310 | 544.8 | 500 | 250 | [8 empty] | 150 | 61 | 76 |  |  |  | 440 | 3.2X104 |  |  | 3.2 | 0.6 |  | 0.8 | [20 empty] | 7 |  |  | 3540 |  | 3.5
[11 empty] | 04.08.2026 | HRL/WW-II/2026/253-254 A dt.11.08.2026 |  | 1: 7.6; 2: 9; 3: 40; 5: 14; 6: 588; 7: 89.9; 8: 341; 9: 112; 18: 52; 19: 36; 20: 48; 23: 280; 24: 270; 25: 90; 28: 3.5; 29: 1; 31: 0.3; 52: BDL(DL=4); 55: 1763 |  | 0.7 |  | Complying | Complying |  | 6.9 | 89 | 296 |  | 192 | 1148 | 244.9 | 451 | 238 | [8 empty] | 142 | 41 | 60 |  |  |  | 320 | 3.4X 10⁴ |  |  | 3.5 | 1 |  | 0.7 | [20 empty] | 20.4 |  |  | 1763 |  | 3.2
49 | (KTL-STP-004) 10 MLD Manas Road,Kaithal by PHED in Sep., 2012 (SBR) |  | 10 | 7 to 8.50 | 100 | 20
[11 empty] | 14.01.2025 | 1891 dt. 21.01.2025 |  | 1: 6.76; 2: 6.8; 3: 44; 5: 12; 11: ND |  |  |  | Complying | Complying |  | 6.6 | 135 | 468 |  | 282 | [5 empty] | 8.29
Under mainatenance
50 | (KTL-STP-005) 7.5 MLD Kaithal by HUDA in 31.8.2016
[11 empty] | 30.01.2026 | 4396 dt. 09.02.2026 |  | 1: 8.13; 2: 7.6; 3: 44; 5: 16; 11: ND |  |  |  | Complying | Complying |  | 6.93 | 120 | 396 |  | 188 | [5 empty] | 13.34
[11 empty] | 24.02.2026 | 4576 dt. 10.03.2026 |  | 1: 7.92; 2: 5.6; 3: 28; 5: 8; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 7.03 | 150 | 508 |  | 352 | [5 empty] | 17.64 | [13 empty] | -
[11 empty] | 18.03.2026 | 4753 dt. 02.04.2026 |  | 1: 7.64; 2: 14; 3: 68; 5: 24; 11: ND; 25: 90 |  |  |  | Non-complying | Non-complying |  | 7.8 | 125 | 432 |  | 211 | [5 empty] | 15.22 | [13 empty] | -
[11 empty] | 08.04.2026 | 59 dt. 23.04.2026 |  | 1: 7.32; 2: 24; 3: 128; 5: 76; 11: 9.68; 25: 500 |  |  |  | Non-complying | Non-complying |  | 7.13 | 185 | 620 |  | 275 | [5 empty] | 19.73 | [13 empty] | -
[11 empty] | 11.05.2026 | HRL/WW-II/2026/53-54 |  | 1: 7.5; 2: 32; 3: 154; 5: 88 |  |  |  | Non-complying | Non-complying
[11 empty] | 05.06.2026 | HRL/WW-II/2026/125-126 A dt. 10.06.2026 |  | 1: 7.8; 2: 30; 3: 124; 5: 82 |  |  |  | Non-complying | Non-complying
| July, 2026 1st Phase | [9 empty] | 03.07.2026 | HRL/WW-II/2026/163-164 A 08.07.2026 |  | 1: 8; 2: 6; 3: 20; 5: 10; 25: 56; 52: BDL |  |  |  | Complying | Complying |  | 7.5 | 118 | 464 |  | 286 | [19 empty] | 2.9X 10⁴ | [26 empty] | 22.4
| July, 2026 2nd Phase | [9 empty] | 16.07.2026 | HRL/WW-II/2026/187-188 A dt. 28.07.2026 |  | 1: 7.3; 2: 16; 3: 56; 5: 24; 6: 1154; 7: 224.9; 8: 244; 9: 118; 18: 119; 19: 19; 20: 160; 23: 200; 24: 160; 25: 1.5X103; 28: 4.6; 29: 5.8; 31: 0.9; 52: BDL(DL=4); 55: 1878 |  | 2.3 |  | Non-complying | Non-complying |  | 7.1 | 84 | 336 |  | 218 | 1228 | 379.9 | 598 | 196 | [8 empty] | 150 | 24 | 40 |  |  |  | 200 | 3.2X 10⁴ |  |  | 4.6 | 5.8 |  | 0.9 | [20 empty] | 5 |  |  | 1878 |  | 3.6
[11 empty] | 04.08.2026 | HRL/WW-II/2026/255-256 A dt.11.08.2026 |  | 1: 7.5; 2: 9; 3: 47; 5: 16; 6: 982; 7: 179.9; 8: 293; 9: 124; 18: 105; 19: 24; 20: 32; 23: 240; 24: 180; 25: 92; 28: 3.4; 29: 1.2; 31: 0.4; 52: BDL(DL=4); 55: 1509 |  | 2.1 |  | Complying | Complying |  | 7.2 | 96 | 320 |  | 220 | 1294 | 279.9 | 634 | 208 | [8 empty] | 158 | 41 | 48 |  |  |  | 290 | 3.8X 10⁴ |  |  | 4 | 4.6 |  | 1.2 | [20 empty] | 18.2 |  |  | 1990 |  | 3.9
51 | (KTL-STP-006) 5 MLD STP Kalayat , Kaithal by PHED in 1.4.2014 |  | 10 | 6.5 to 9 | 50 | 20
[11 empty] | 09.01.2026 | 4270 dt.21.01.2026 | 111.65 | 1: 7.46; 2: 5.2; 3: 44; 5: 13; 11: ND |  |  |  | Complying | Complying | 120.35 | 7.24 | 135 | 456 |  | 302 | [5 empty] | 14.86
[11 empty] | 24.02.2026 | 4578 dt. 10.03.2026 | 110.55 | 1: 7.43; 2: 6.2; 3: 32; 5: 11; 11: ND; 25: 60 |  |  |  | Complying | Complying | 119.25 | 7.23 | 140 | 496 |  | 293 | [5 empty] | 12.59 | [13 empty] | -
[11 empty] | 18.03.2026 | 4747 dt. 02.04.2026 | 11115 | 1: 7.73; 2: 7.6; 3: 48; 5: 14; 11: ND; 25: 90 |  |  |  | Complying | Complying | 121.25 | 7.89 | 110 | 384 |  | 184 | [5 empty] | 13.68 | [13 empty] | -
[11 empty] | 08.04.2026 | 64 dt. 23.04.2026 | 112.25 | 1: 7.56; 2: 7.5; 3: 40; 5: 13; 11: ND; 25: 80 |  |  |  | Complying | Complying | 122.67 | 7.15 | 110 | 380 |  | 174 | [5 empty] | 14.79 | [13 empty] | -
[11 empty] | 11.05.2026 | HRL/WW-II/2026/41-42 | 108.12 | 1: 7.5; 2: 8; 3: 38; 5: 16 |  |  |  | Complying | Complying | 120.3 | 7.4 | 96 | 314 |  | 204
[11 empty] | 04.06.2026 | HRL/WW-II/2026/116 -117 A dt. 10.06.2026 |  | 1: 8.4; 2: 6; 3: 36; 5: 16 |  |  |  | Complying | Complying |  | 7.8 | 98 | 320 |  | 232
| July, 2026 1st Phase | [9 empty] | 02.07.2026 | HRL/WW-II/2026/157-158 A 08.07.2026 | 113.24 | 1: 8; 2: 7; 3: 32; 5: 14; 25: 70; 52: BDL |  |  |  | Complying | Complying | 124.56 | 7.7 | 96 | 328 |  | 248 | [19 empty] | 3.3 X 10⁴ | [26 empty] | 20.8
| July, 2026 2nd Phase | [9 empty] | 16.07.2026 | HRL/WW-II/2026/183-184 A dt. 28.07.2026 |  | 1: 7.3; 2: 9; 3: 48; 5: 14; 6: 964; 7: 229.9; 8: 476; 9: 115; 18: 115; 19: 39; 20: 270; 23: 390; 24: 270; 25: 90; 28: 3; 29: 2.4; 31: 0.3; 52: BDL(DL=4); 55: 1478 |  | 2.6 |  | Complying | Complying |  | 7 | 76 | 288 |  | 204 | 2358 | 519.8 | 573 | 198 | [8 empty] | 160 | 70 | 80 |  |  |  | 490 | 3.1X 10⁴ |  |  | 3.2 | -0.4 |  | 1 | [20 empty] | 3 |  |  | 3620 |  | 3.5
[11 empty] | 04.08.2026 | HRL/WW-II/2026/249-250 A dt. 10.08.2026 |  | 1: 7; 2: 6; 3: 32; 5: 10; 25: 86; 52: BDL(DL=4); 55: 1254 |  |  |  | Complying | Complying |  | 7.1 | 94 | 312 |  | 236 | [19 empty] | 3.4X 10⁴ | [26 empty] | 20.8 |  |  | 3462
52 | (KTL-STP-007) 3.5 Pundri Kaithal by PHED in 4.7.2014 |  | 20 | 7 to 8 | 50 | 40
[11 empty] | 22.01.2026 | 4351 dt. 03.02.2026 | - | 1: 7.54; 2: 5.6; 3: 36; 5: 11; 11: ND |  |  |  | Complying | Complying | 115.6 | 7.12 | 108 | 380 |  | 234 | [5 empty] | 16.73
[11 empty] | 24.02.2026 | 4577 dt. 10.03.2026 | 72.3 | 1: 7.92; 2: 5.6; 3: 28; 5: 8; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 7.23 | 150 | 508 |  | 352 | [5 empty] | 17.64 | [13 empty] | -
[11 empty] | 18.03.2026 | 4749 dt. 02.04.2026 | 102 | 1: 7.2; 2: 5; 3: 36; 5: 7; 11: ND; 25: 50 |  |  |  | Complying | Complying | 120 | 7.59 | 160 | 524 |  | 338 | [5 empty] | 13.78 | [13 empty] | -
[11 empty] | 08.04.2026 | 66 dt. 23.04.2026 |  | 1: 7.9; 2: 5.8; 3: 28; 5: 12; 11: ND; 25: 70 |  |  |  | Complying | Complying |  | 7.13 | 120 | 392 |  | 118 | [5 empty] | 15.08 | [13 empty] | -
[11 empty] | 11.05.2026 | HRL/WW-II/2026/55-56 | 101 | 1: 7.6; 2: 5; 3: 22; 5: 12 |  |  |  | Complying | Complying | 118 | 7.2 | 102 | 324 |  | 186
[11 empty] | 4.06.2026 | HRL/WW-II/2026/120 -121 A dt. 10.06.2026 |  | 1: 8.4; 2: 6; 3: 28; 5: 14 |  |  |  | Complying | Complying
| July, 2026 1st Phase | [9 empty] | 02.07.2026 | HRL/WW-II/2026/159-160 A 08.07.2026 | 102 | 1: 8.1; 2: 5; 3: 24; 5: 12; 25: 76; 52: BDL |  |  |  | Complying | Complying | 114 | 7.8 | 96 | 312 |  | 208 | [19 empty] | 3.5 X 10⁴ | [26 empty] | 20.4
| July, 2026 2nd Phase | [9 empty] | 16.07.2026 | HRL/WW-II/2026/185-186 A dt. 28.07.2026 |  | 1: 7.4; 2: 8; 3: 48; 5: 16; 6: 962; 7: 234.9; 8: 378; 9: 110; 18: 118; 19: 29; 20: 200; 23: 310; 24: 200; 25: 86; 28: 3.6; 29: 2.2; 31: 0.2; 52: BDL(DL=4); 55: 1480 |  | 2.2 |  | Complying | Complying |  | 7 | 78 | 296 |  | 192 | 2248 | 549.8 | 464 | 184 |  | 370 | [6 empty] | 155 | 53 | 60 |  |  |  | 370 | 2.7X 10⁴ |  |  | 3.4 | 0.3 |  | 0.8 | [20 empty] | 4 |  |  | 3458 |  | 3.2
[11 empty] | 04.08.2026 | HRL/WW-II/2026/247-248 A dt. 10.08.2026 |  | 1: 7; 2: 7; 3: 32; 5: 12; 25: 82; 52: BDL(DL=4); 55: 1285 |  |  |  | Complying | Complying |  | 7.1 | 80 | 304 |  | 226 | [19 empty] | 2.9X 10⁴ | [26 empty] | 18.2 |  |  | 3548
53 | 3 MLD, STP, PHED, SBR Village Keorak Distt Kaithal | [83 empty] | 11.22
[11 empty] | 30.01.2026 | 4393 dt. 09.02.2026 |  | 1: 7.9; 2: 7.8; 3: 44; 5: 16; 11: ND |  |  |  | Complying | Complying |  | 7 | 140 | 492 |  | 252 | [5 empty] | 13.54
[11 empty] | 18.02.2026 | 4546 dt. 03.03.2026 | 38.7 | 1: 7.89; 2: 7.2; 3: 40; 5: 13; 11: 2.72; 25: 80 |  |  |  | Complying | Complying |  | 7.56 | 120 | 400 |  | 178 | [5 empty] | 14.72 | [13 empty] | -
[11 empty] | 18.03.2026 | 4751 dt. 02.04.2026 | 27.8 | 1: 7.02; 2: 5.8; 3: 40; 5: 9; 11: ND; 25: 70 |  |  |  | Complying | Complying |  | 6.89 | 120 | 432 |  | 198 | [5 empty] | 13.28 | [13 empty] | -
[11 empty] | 08.04.2026 | 60 dt. 23.04.2026 |  | 1: 7.01; 2: 6.5; 3: 32; 5: 11; 11: ND; 25: 60 |  |  |  | Complying | Complying |  | 6.9 | 108 | 348 |  | 142 | [5 empty] | 14.84 | [13 empty] | -
[11 empty] | 11.05.2026 | HRL/WW-II/2026/49-50 |  | 1: 7.5; 2: 6; 3: 28; 5: 12 |  |  |  | Complying | Complying |  | 7.2 | 102 | 320 |  | 188
[11 empty] | 10.06.2026 | HRL/WW-II/2026/110-111 A | 41.059 | 1: 7.8; 2: 5; 3: 24; 5: 10 |  |  |  | Complying | Complying | 94.5 | 7.7 | 107 | 312 |  | 206
| July, 2026 1st Phase | [9 empty] | 03.07.2026 | HRL/WW-II/2026/161-162 A 08.07.2026 | 14.6 | 1: 8.4; 2: 5; 3: 20; 5: 8; 25: 68; 52: BDL |  |  |  | Complying | Complying | 18.8 | 7.9 | 110 | 344 |  | 230 | [19 empty] | 2.8X 10⁴
| July, 2026 2nd Phase | [9 empty] | 16.07.2026 | HRL/WW-II/2026/189-190 A dt. 28.07.2026 |  | 1: 7.3; 2: 9; 3: 48; 5: 12; 6: 948; 7: 84.9; 8: 488; 9: 128; 18: 55; 19: 29; 20: 210; 23: 400; 24: 210; 25: 92; 28: 1.6; 29: 3.8; 31: 0.3; 52: BDL(DL=4); 55: 1450 |  | 1.1 |  | Complying | Complying |  | 7 | 72 | 280 |  | 186 | 2278 | 594.7 | 561 | 128 | [8 empty] | 55 | 56 | 60 |  |  |  | 380 | 2.8X104 |  |  | 3.5 | 0.8 |  | 0.7 | [20 empty] | 6 |  |  | 3504 |  | 1.1
[11 empty] | 04.08.2026 | HRL/WW-II/2026/257-258 A dt.11.08.2026 | 187.7 | 1: 7.6; 2: 8; 3: 32; 5: 12; 6: 594; 7: 94.9; 8: 439; 9: 122; 18: 53; 19: 39; 20: 44; 23: 410; 24: 270; 25: 190; 28: 9.3; 29: 2.8; 31: 0.8; 52: BDL(DL=4); 55: 1780 |  | 3.6 |  | Complying | Complying | 205.7 | 7.1 | 92 | 304 |  | 208 | 1158 | 254.9 | 500 | 254 | [8 empty] | 139 | 39 | 44 |  |  |  | 270 | 3.1X 10⁴ |  |  | 9.3 | 2.8 |  | 0.8 | [20 empty] | 16.4 |  |  | 1780 |  | 3.6
54 | 3.5 MLD STP based on SBR Technology, Pilni Road, Village Pai, Tehsil Pundri District Kaithal
[11 empty] | 22.01.2026 | 4352 dt. 03.02.2026 | 2.506 | 1: 7.75; 2: 7.5; 3: 40; 5: 15; 11: ND |  |  |  | Complying | Complying | 3.29 | 7.14 | 120 | 400 |  | 230 | [5 empty] | 16.22
[11 empty] | 24.02.2026 | 4575 dt. 10.03.2026 |  | 1: 7.79; 2: 7.6; 3: 40; 5: 15; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 7.05 | 102 | 380 |  | 125 | [5 empty] | 13.76 | [13 empty] | -
[11 empty] | 18.03.2026 | 4748 dt. 02.04.2026 | 128.7 | 1: 7.89; 2: 7; 3: 44; 5: 9; 11: ND; 25: 70 |  |  |  | Complying | Complying | 139.3 | 7.86 | 102 | 344 |  | 175 | [5 empty] | 14.72 | [13 empty] | -
[11 empty] | 11.05.2026 | HRL/WW-II/2026/51-52 |  | 1: 7.8; 2: 7; 3: 34; 5: 14 |  |  |  | Complying | Complying |  | 7.2 | 92 | 304 |  | 174
[11 empty] | 04.06.2026 | HRL/WW-II/2026/118 -119 A 10.06.2026 |  | 1: 8.4; 2: 5; 3: 28; 5: 12 |  |  |  | Complying | Complying
| July, 2026 1st Phase | [9 empty] | 02.07.2026 | HRL/WW-II/2026/155-156 A 08.07.2026 | 28.359 | 1: 8.1; 2: 5; 3: 24; 5: 10; 25: 68; 52: BDL |  |  |  | Complying | Complying | 32.122 | 7.6 | 94 | 320 |  | 216 | [19 empty] | 2.9X 10⁴ | [26 empty] | 22.4
| July, 2026 2nd Phase | [9 empty] | 16.07.2026 | HRL/WW-II/2026/181-182 A dt. 28.07.2026 |  | 1: 7.4; 2: 18; 3: 68; 5: 24; 6: 976; 7: 239.9; 8: 293; 9: 120; 18: 120; 19: 41; 20: 280; 23: 240; 24: 280; 25: 1.6X103; 28: 3.1; 29: -0.8; 31: 0.2; 52: BDL(DL=4); 55: 1492 |  | 2.6 |  | Non-Complying | Non-Complying |  | 7.5 | 83 | 312 |  | 196 | 2282 | 629.8 | 378 | 192 | [8 empty] | 150 | 61 | 64 |  |  |  | 410 | 2.9X 10⁴ |  |  | 3.2 | -2 |  | 0.9 | [20 empty] | 2 |  |  | 3518 |  | 3.8
[11 empty] | 04.08.2026 | HRL/WW-II/2026/243-244 A dt. 10.08.2026 |  | 1: 7.2; 2: 8; 3: 32; 5: 14; 25: 76; 52: BDL(DL=4); 55: 1650 |  |  |  | Complying | Complying |  | 7.1 | 94 | 312 |  | 226 | [19 empty] | 3.4X 10⁴ | [26 empty] | 18.4 |  |  | 1984
Hisar
55 | (HSR-STP-001) 15 MLD STP Azad Nagar, Rajgarh Road Hisar by PHED in 31.12.2014 |  | 10 | 6.5 to 8 | 100 | 10
[11 empty] | 06.01.2026 | 4212 dt. 15.01.2026 | 11.27 | 1: 6.89; 2: 7; 3: 40; 5: 11; 11: ND |  |  |  | Complying | Complying | 11.42 | 7.13 | 135 | 480 |  | 248 | [5 empty] | 14.59
[11 empty] | 12.02.2026 | 4518 dt. 02.03.2026 |  | 1: 7.65; 2: 5.8; 3: 40; 5: 11; 11: 1.96; 25: 90 |  |  |  | Complying | Complying |  | 7.89 | 110 | 380 |  | 195 | [5 empty] | 15.68
[11 empty] | 27.03.2026 | 4782 dt. 08.04.2026 | 12.4 | 1: 7.52; 2: 8.6; 3: 48; 5: 11; 11: 1.97; 25: 90 |  |  |  | Complying | Complying | 12.98 | 7.64 | 160 | 572 |  | 248 | [5 empty] | 15.68
[11 empty] | 07.04.2026 | 54 dt. 22.04.2026 | 11.2 | 1: 7.74; 2: 7; 3: 48; 5: 11; 11: ND; 25: 70 |  |  |  | Complying | Complying | 11.42 | 6.89 | 102 | 316 |  | 175 | [5 empty] | 13.56
[11 empty] | 07.05.2026 | 210 dt. 18.05.2026 |  | 1: 8.79; 2: 5.8; 3: 28; 5: 17; 11: 1.85; 25: 80 |  |  |  | Complying | Complying |  | 7.94 | 82 | 284 |  | 78 | [5 empty] | BDL | [13 empty] | -
[11 empty] | 10.06.2026 | 326-327A dt. 16.06.2026 |  | 1: 7.4; 2: 8.6; 3: 44; 5: 12; 11: 8.6; 25: 56 |  |  |  | Complying | Complying |  | 8.8 | 106 | 428 |  | 216 | [5 empty] | 28.4 | [13 empty] | 24000
[11 empty] | 06.07.2026 | 415-416A dt. 14.07.2026 |  | 1: 7.9; 2: 8.8; 3: 48; 5: 18; 11: 9; 25: 86; 52: BDL |  |  |  | Complying | Complying |  | 8.6 | 112 | 444 |  | 232 | [5 empty] | 32 | [13 empty] | 32000
[11 empty] | 20.07.2026 | 520-21 dt. 30.07.2026 |  | 1: 7.9; 2: 8; 3: 48; 5: 18; 25: 72; 52: 5 |  |  |  | Complying | Complying |  | 7.7 | 56 | 140 |  | 188 | [19 empty] | 65000 | [26 empty] | 42
[11 empty] | 07.08.2026 | 724 dt. 21.08.2026 |  | 1: 7.3; 2: 9.2; 3: 48; 5: 16; 25: 36; 52: BDL |  |  |  | Complying | Complying |  | 7.8 | 86 | 136 |  | 142 | [19 empty] | 42000 | [26 empty] | 30
56 | (HSR-STP-002) 40 MLD STP Rishi Nagar, Hisar by PHED in 02.12.2017 | PHED | 5 | 5.5 to 9 | 50 | 5
[11 empty] | 06.01.2026 | 4209 dt.15.01.2026 | 34.02 | 1: 7.23; 2: 7.5; 3: 48; 5: 13; 11: ND |  |  |  | Complying | Complying | 34.48 | 7.05 | 112 | 388 |  | 185 | [5 empty] | 14.32
[11 empty] | 03.02.2026 | 4428 dt. 16.02.2026 |  | 1: 7.44; 2: 7.8; 3: 48; 5: 15; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 7.19 | 135 | 460 |  | 138 | [5 empty] | 15.28
[11 empty] | 12.03.2026 | 4699 dt. 25.03.2026 |  | 1: 7.8; 2: 6; 3: 32; 5: 9.5; 11: ND; 25: 50 |  |  |  | Complying | Complying |  | 7.57 | 110 | 360 |  | 172 | [5 empty] | 15.92
[11 empty] | 02.04.2026 | 35 dt. 17.04.2026 | 33.2 | 1: 7.43; 2: 6.8; 3: 44; 5: 13; 11: ND; 25: 70 |  |  |  | Complying | Complying | 33.4 | 7.36 | 120 | 408 |  | 218 | [5 empty] | 13.84
[11 empty] | 21.05.2026 | 183-184A dt. 26.05.2026 |  | 1: 7.8; 2: 8.2; 3: 35; 5: 15; 11: ND; 25: 96 |  |  |  | Complying | Complying |  | 8.7 | 105 | 360 |  | 224 | [5 empty] | ND | [13 empty] | 36000
[11 empty] | 09.06.2026 | 301-302A dt. 16.06.2026 |  | 1: 7.6; 2: 7.9; 3: 32; 5: 14; 11: 8; 25: 72 |  |  |  | Complying | Complying |  | 8.4 | 240 | 408 |  | 188 | [5 empty] | 32.4 | [13 empty] | 39000
[11 empty] | 02.07.2026 | 396-397A dt. 08.07.2026 |  | 1: 7.4; 2: 7.8; 3: 36; 5: 9; 11: 12; 25: 48; 52: BDL |  |  |  | Complying | Complying |  | 6.5 | 82 | 152 |  | 146 | [5 empty] | 76 | [13 empty] | 12000 | [26 empty] | 25
[11 empty] | 20.07.2026 | 528-29 dt. 30.07.2026 |  | 1: 7.9; 2: 9.2; 3: 48; 5: 18; 11: 80; 52: BDL |  |  |  | Complying | Complying |  | 7.7 | 108 | 208 |  | 212 | [19 empty] | 56000 | [26 empty] | 22
[11 empty] | 03.08.2026 | 639-40 dt. 11.08.2026 |  | 1: 6.2; 2: 102; 3: 464; 5: 45; 11: 12000; 52: 18 |  |  |  | Non Complying | Non Complying |  | 8.9 | 148 | 560 |  | 168 | [19 empty] | 48000 | [26 empty] | 32
57 | (HSR-STP-003) 4 MLD STP Narnaund, Hisar by PHED 31.03.2019 |  | 10 | 5.5 to 9 | 100 | 10
[11 empty] | 28.01.2026 | 4376 dt. 09.02.2026 | 1.82 | 1: 7.22; 2: 7.6; 3: 44; 5: 15; 11: ND |  |  |  | Complying | Complying | 1.98 | 7.57 | 125 | 408 |  | 215 | [5 empty] | 15.26
[11 empty] | 20.02.2026 | 4567 dt. 10.03.2026 |  | 1: 7.56; 2: 7.2; 3: 48; 5: 15; 11: 2.82; 25: 90 |  |  |  | Complying | Complying |  | 7.75 | 130 | 460 |  | 256 | [5 empty] | 17.92
[11 empty] | 17.03.2026 | 4746 dt. 02.04.2026 |  | 1: 7.6; 2: 5.4; 3: 36; 5: 11; 11: 1.98; 25: 70 |  |  |  | Complying | Complying |  | 7.89 | 130 | 440 |  | 215 | [5 empty] | 12.92
[11 empty] | 23.04.2026 | 9-10A dt. 28.04.2026 |  | 1: 6.9; 2: 7; 3: 44; 5: 12; 25: 70 |  |  |  | Complying | Complying |  | 7 | 188 | 466 |  | 296
[11 empty] | 27.05.2026 | 214-215A dt. 04.06.2026 |  | 1: 7.4; 2: 8.8; 3: 42; 5: 12; 11: NA; 25: 80 |  |  |  | Complying | Complying |  | 8.3 | 152 | 408 |  | 242 | [5 empty] | ND | [13 empty] | 24000
[11 empty] | 10.06.2026 | 309-310A dt. 16.06.2026 |  | 1: 7.8; 2: 8.4; 3: 32; 5: 12; 25: 80 |  |  |  | Complying | Complying |  | 8.8 | 108 | 376 |  | 212 | [19 empty] | 42000
[11 empty] | 06.07.2026 | 417-418A dt. 14.07.2026 |  | 1: 7.6; 2: 8.8; 3: 40; 5: 14; 11: 8; 25: 90; 52: BDL |  |  |  | Complying | Complying |  | 8.5 | 112 | 392 |  | 236 | [5 empty] | 26 | [13 empty] | 45000 | [26 empty] | 32
[11 empty] | 16.07.2026 | 511-12 dt. 30.07.2026 |  | 1: 8.4; 2: 22; 3: 84; 5: 42; 25: 1800; 52: 7 |  |  |  | Non-complying | Non-complying |  | 8.1 | 168 | 304 |  | 256 | [19 empty] | 48000 | [26 empty] | 45
[11 empty] | 04.08.2026 | 678-79 dt. 11.08.2026 |  | 1: 7.7; 2: 9; 3: 44; 5: 16; 25: 32; 52: BDl |  |  |  | Complying | Complying |  | 8.9 | 104 | 168 |  | 164 | [19 empty] | 36000 | [26 empty] | 25
58 | (HSR-STP-004) 15 MLD STP, Dabara Tosham Road , Hisar by HUDA in 31.7.2014
[11 empty] | 29.01.2026 | 4381 dt. 09.02.2026 | 9.89 | 1: 7.85; 2: 7.2; 3: 36; 5: 9; 11: ND |  |  |  | Complying | Complying | 10.98 | 7.53 | 102 | 352 |  | 175 | [5 empty] | 13.46
[11 empty] | 26.02.2026 | 4603 dt. 11.03.2026 |  | 1: 7.49; 2: 7.8; 3: 44; 5: 12; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 7.43 | 120 | 396 |  | 158 | [5 empty] | 12.46
[11 empty] | 27.03.2026 | 4781 dt. 08.04.2026 | 10.98 | 1: 8.14; 2: 7.2; 3: 40; 5: 12; 11: 2.78; 25: 70 |  |  |  | Complying | Complying | 11 | 7.4 | 170 | 480 |  | 198 | [5 empty] | 18.39
[11 empty] | 07.04.2026 | 55 dt. 22.04.2026 | 12.22 | 1: 7.53; 2: 7.2; 3: 44; 5: 15; 11: ND; 25: 80 |  |  |  | Complying | Complying | 12.47 | 7.02 | 210 | 704 |  | 292 | [5 empty] | 17.24
[11 empty] | 01.05.2026 | 27-28A dt. 08.05.2026 |  | 1: 7; 2: 7; 3: 36; 5: 13; 11: ND; 25: 86 |  |  |  | Complying | Complying |  | 7.9 | 82 | 392 |  | 296 | [5 empty] | ND | [13 empty] | 96000
[11 empty] | 07.05.2026 | 211 dt. 18.05.2026 |  | 1: 8.14; 2: 8.8; 3: 44; 5: 16; 11: 8.35; 25: 1200 |  |  |  | Complying | Complying |  | 7.93 | 98 | 348 |  | 450 | [5 empty] | 2.43 | [13 empty] | -
[11 empty] | 10.06.2026 | 330-331A dt. 22.06.2026 |  | 1: 7.1; 2: 7.8; 3: 40; 5: 11; 25: 90 |  |  |  | Complying | Complying |  | 7.5 | 92 | 408 |  | 278 | [19 empty] | 13.6
[11 empty] | 06.07.2026 | 408-409A dt. 14.07.2026 |  | 1: 7.4; 2: 8.4; 3: 40; 5: 17; 11: 8; 25: 86; 52: BDL |  |  |  | Complying | Complying |  | 7.8 | 86 | 392 |  | 240 | [5 empty] | 22 | [13 empty] | 72000 | [26 empty] | 23
[11 empty] | 20.07.2026 | 524-25 dt 30.07.2026 |  | 1: 7.9; 2: 8.2; 3: 40; 5: 15; 25: 76; 52: 4 |  |  |  | Complying | Complying |  | 7.8 | 42 | 144 |  | 178 | [5 empty] | 37 | [13 empty] | 72000
[11 empty] | 07.08.2026 | 720-721A dt. 21.08.2026 |  | 1: 7.8; 2: 6.5; 3: 36; 5: 14; 25: 65; 52: BDL |  |  |  | Complying | Complying |  | 7.7 | 62 | 176 |  | 172 | [19 empty] | 56000 | [26 empty] | 28
59 | (HSR-STP-005) 4 MLD STP, Kaimri Road, Hisar by PHED in 2018 | PHED | 10 | 5.5 to 9 | 100 | 10
[11 empty] | 29.01.2026 | 4380 dt. 09.02.2026 | 2.07 | 1: 7.59; 2: 9; 3: 60; 5: 28; 11: ND |  |  |  | Non-complying | Non-complying | 2.28 | 7.49 | 135 | 452 |  | 134 | [5 empty] | 14.52
[11 empty] | 03.02.2026 | 4425 dt.16.02.2026 |  | 1: 7.67; 2: 18; 3: 68; 5: 27; 11: 8.28; 25: 400 |  |  |  | Non-complying | Non-complying |  | 7.01 | 130 | 452 |  | 186 | [5 empty] | 15.67
[11 empty] | 12.03.2026 | 4698 dt. 25.03.2026 |  | 1: 8.1; 2: 42; 3: 192; 5: 25; 11: 11.24; 25: 800 |  |  |  | Non-complying | Non-complying |  | 7.34 | 110 | 384 |  | 172 | [5 empty] | 17.82
[11 empty] | 02.04.2026 | 37 dt. 17.04.2026 |  | 1: 7.53; 2: 72; 3: 268; 5: 188; 11: 19.74; 25: 1400 |  |  |  | Non-complying | Non-complying
[11 empty] | 12.05.2026 | 103-104A dt. 20.05.2026 | Bypass | 1: 8.8; 2: 80; 3: 256; 5: 204; 11: 12.6; 25: 52000 |  |  |  | Non-complying | Non-complying |  | 8.9 | 96 | 288 |  | 346 | [5 empty] | 38.4 | [13 empty] | 56000
[11 empty] | 10.06.2026 | 323A dt. 16.06.2026 | Bypass | 1: 8.5; 2: 72; 3: 320; 5: 64; 11: 38.4; 25: 72000 |  |  |  | Non-complying | Non-complying
[11 empty] | 06.07.2026 | 412A dt. 14.07.2026 | Bypass | 1: 8.6; 2: 106; 3: 496; 5: 72; 11: 42.4; 25: 1200 |  |  |  | Non-complying | Non-complying
[11 empty] | 20.07.2026 | 519A dt. 30.07.2026 | Bypass | 1: 8.9; 2: 26; 3: 96; 5: 96; 11: 18; 25: 72000 |  |  |  | Non-complying | Non-complying
[11 empty] | 07.08.2026 | 722 dt. 21.08.2026 |  | 1: 8.4; 2: 96; 3: 176; 5: 224; 25: 48000; 52: 24 |  |  |  | Non-complying | Non-complying
60 | (HSR-STP-011) 8 MLD STP Village Satrod, Dabra Road, Hisar by ULBD in 31.03.2021
[11 empty] | 06.01.2026 | 4211 dt. 15.01.2026 | 4.02 | 1: 7.93; 2: 7.5; 3: 44; 5: 15; 11: ND |  |  |  | Complying | Complying | 4.22 | 7.29 | 125 | 408 |  | 215 | [5 empty] | 13.32
[11 empty] | 12.02.2026 | 4517 dt. 02.03.2026 |  | 1: 7.79; 2: 5.5; 3: 32; 5: 8; 11: 2.52; 25: 80 |  |  |  | Complying | Complying |  | 8.29 | 120 | 432 |  | 210 | [5 empty] | 14.56
[11 empty] | 27.03.2026 | 4786 dt. 08.04.2026 | 4.36 | 1: 7.36; 2: 6.8; 3: 40; 5: 17; 11: 2.48; 25: 50 |  |  |  | Complying | Complying | 4.48 | 7.84 | 130 | 432 |  | 246 | [5 empty] | 15.48
[11 empty] | 07.04.2026 | 56 dt. 22.04.2026 | 3.92 | 1: 7.29; 2: 7.2; 3: 40; 5: 16; 11: ND; 25: 90 |  |  |  | Complying | Complying | 4 | 7.12 | 145 | 504 |  | 208 | [5 empty] | 14.97
[11 empty] | 01.05.2026 | 25-26A dt. 08.05.2026 |  | 1: 7.2; 2: 7; 3: 32; 5: 14; 11: ND; 25: 48 |  |  |  | Complying | Complying |  | 7.8 | 105 | 380 |  | 396 | [5 empty] | ND | [13 empty] | 12000
[11 empty] | 07.05.2026 | 212 dt. 18.05.2026 |  | 1: 8.27; 2: 6.4; 3: 32; 5: BDL; 11: 0.699; 25: 90 |  |  |  | Complying | Complying |  | 7.89 | 84 | 276 |  | 316 | [5 empty] | 1.35 | [13 empty] | -
[11 empty] | 10.06.2026 | 328-329A dt. 16.06.2026 |  | 1: 7.2; 2: 7.2; 3: 36; 5: 18; 11: 9.2; 25: 82 |  |  |  | Complying | Complying |  | 8.2 | 110 | 416 |  | 232 | [5 empty] | 24.2 | [13 empty] | 15000
[11 empty] | 06.07.2026 | 410-411 dt. 14.07.2026 |  | 1: 7; 2: 7.4; 3: 44; 5: 22; 11: 9; 25: 72; 52: BDL |  |  |  | Complying | Complying |  | 8.2 | 102 | 408 |  | 240 | [5 empty] | 26 | [13 empty] | 28000 | [26 empty] | 34
[11 empty] | 20.07.2026 | 522-23 dt. 30.07.2026 |  | 1: 7.8; 2: 7.8; 3: 42; 5: 14; 25: 56; 52: 6 |  |  |  | Complying | Complying |  | 7.6 | 72 | 184 |  | 170 | [19 empty] | 48000 | [26 empty] | 32
[11 empty] | 03.08.2026 | 643-44 dt 11.08.2026 |  | 1: 7.9; 2: 14; 3: 72; 5: 24; 25: 620; 52: 8 |  |  |  | Non complying | Non complying |  | 8.2 | 108 | 192 |  | 128 | [19 empty] | 32000 | [26 empty] | 34
61 | (HSR-STP-012)15 MLD STP, Hisar Sector-14, New Rishi Nagar, Hisar by HSVP in 31.05.2024
[11 empty] | 06.01.2026 | 4210 dt.15.01.2026 | 3.55 | 1: 7.23; 2: 7.2; 3: 44; 5: 12; 11: ND |  |  |  | Complying | Complying | 3.83 | 7.08 | 130 | 452 |  | 214 | [5 empty] | 14.92
[11 empty] | 03.02.2026 | 4427 dt. 16.02.2026 |  | 1: 7.09; 2: 6.8; 3: 40; 5: 12; 11: ND; 25: 70 |  |  |  | Complying | Complying |  | 7.08 | 120 | 396 |  | 218 | [5 empty] | 14.53
[11 empty] | 12.03.2026 | 4697 dt. 25.03.2026 |  | 1: 7.46; 2: 7.8; 3: 48; 5: 11; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 7.56 | 130 | 424 |  | 185 | [5 empty] | 13.47
[11 empty] | 02.04.2026 | 36 dt. 17.04.2026 | 4.3 | 1: 7.92; 2: 8.5; 3: 48; 5: 17; 11: ND; 25: 60 |  |  |  | Complying | Complying | 4.48 | 7.28 | 122 | 416 |  | 240 | [5 empty] | 17.33
[11 empty] | 27.05.2026 | 218-219A dt. 04.06.2026 |  | 1: 7.9; 2: 7.8; 3: 40; 5: 15; 11: ND; 25: 86 |  |  |  | Complying | Complying |  | 8.4 | 156 | 528 |  | 262 | [5 empty] | ND | [13 empty] | 35000
[11 empty] | 09.06.2026 | 303-304A dt. 16.06.2026 |  | 1: 7.3; 2: 7.2; 3: 28; 5: 16; 11: 6.8; 25: 56 |  |  |  | Complying | Complying |  | 8.2 | 90 | 280 |  | 248 | [5 empty] | 28 | [13 empty] | 42000
[11 empty] | 02.07.2026 | 398-399A dt. 08.07.2026 |  | 1: 7.4; 2: 8.2; 3: 40; 5: 12; 11: 28; 25: 32; 52: BDL |  |  |  | Complying | Complying |  | 7.6 | 96 | 196 |  | 112 | [5 empty] | 52 | [13 empty] | 28000 | [26 empty] | 28
[11 empty] | 20.07.2026 | 530-31 dt. 30.07.2026 |  | 1: 7.6; 2: 7.2; 3: 32; 5: 11; 25: 62; 52: BDL |  |  |  | Complying | Complying |  | 7.9 | 96 | 148 |  | 148 | [19 empty] | 64000 | [26 empty] | 28
[11 empty] | 03.08.2026 | 641-42 dt. 11.08.2026 |  | 1: 7.8; 2: 8.6; 3: 42; 5: 18; 25: 45; 52: 6 |  |  |  | Complying | Complying |  | 8.3 | 106 | 248 |  | 170 | [19 empty] | 42000 | [26 empty] | 36
62 | 5 MLD STP Hisar by PHED in 31.03.2025 (New)
[11 empty] | 06.01.2026 | 4213 dt. 15.01.2026 |  | 1: 7.48; 2: 7.6; 3: 48; 5: 12; 11: ND |  |  |  | Complying | Complying | 1.2 | 7.28 | 125 | 428 |  | 192 | [5 empty] | 13.69
[11 empty] | 26.02.2026 | 4602 dt. 11.03.2026 |  | 1: 7.9; 2: 9.5; 3: 48; 5: 17; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 7.87 | 120 | 408 |  | 178 | [5 empty] | 14.39
[11 empty] | 27.03.2026 | 4779 dt. 08.04.2026 | 1.8 | 1: 7.87; 2: 7.6; 3: 40; 5: 16; 11: ND; 25: 50 |  |  |  | Complying | Complying | 1.98 | 7.68 | 106 | 344 |  | 156 | [5 empty] | 14.98
[11 empty] | 07.04.2026 | 57 dt. 22.04.2026 | 1.22 | 1: 7.26; 2: 8.2; 3: 48; 5: 15; 11: ND; 25: 80 |  |  |  | Complying | Complying | 1.42 | 6.76 | 125 | 436 |  | 210 | [5 empty] | 13.72
[11 empty] | 01.05.2026 | 23-24A dt. 08.05.2026 |  | 1: 7.2; 2: 8; 3: 36; 5: 12; 11: ND; 25: 72 |  |  |  | Complying | Complying |  | 8.2 | 126 | 420 |  | 274 | [5 empty] | ND | [13 empty] | 15000
[11 empty] | 10.06.2026 | 324-325A dt. 16.06.2026 |  | 1: 7.7; 2: 8.2; 3: 40; 5: 14; 11: 18.2; 25: 72 |  |  |  | Complying | Complying |  | 8.4 | 116 | 396 |  | 258 | [5 empty] | 32.4 | [13 empty] | 18000
[11 empty] | 06.07.2026 | 413-414A dt. 14.07.2026 |  | 1: 7.6; 2: 7.6; 3: 32; 5: 12; 11: 16; 25: 56; 52: BDL |  |  |  | Complying | Complying |  | 8.2 | 110 | 380 |  | 224 | [5 empty] | 30 | [13 empty] | 15000 | [26 empty] | 20
[11 empty] | 06.07.2026 | 413-414A dt. 14.07.2026 |  | 1: 7.6; 2: 7.6; 3: 32; 5: 12; 11: 16; 25: 56; 52: BDL |  |  |  | Complying | Complying |  | 8.2 | 110 | 380 |  | 224 | [5 empty] | 30 | [13 empty] | 15000 | [26 empty] | 20
[11 empty] | 20.07.2026 | 526-27 dt. 30.07.2026 |  | 1: 7.5; 2: 8.2; 3: 44; 5: 12; 25: 72; 52: BDL |  |  |  | Complying | Complying |  | 7.4 | 92 | 128 |  | 122 | [19 empty] | 48000 | [26 empty] | 26
[11 empty] | 07.08.2026 | 726-27 dt. 21.08.2026 |  | 1: 7.3; 2: 8.6; 3: 44; 5: 14; 25: 56; 52: BDL |  |  |  | Complying | Complying |  | 7.6 | 42 | 120 |  | 148 | [19 empty] | 52000 | [26 empty] | 18
Sirsa
63 | (SRS-STP-001) 15 MLD STP, Shamsabad patti, Kalania Road, Sirsa by PHED in 1.7.2012 |  | 20 | 6.5 to 9 | 50 | 20
[11 empty] | 07.01.2026 | 4253 dt. 20.01.2026 | 9.23 | 1: 7.24; 2: 6.4; 3: 36; 5: 9; 11: ND |  |  |  | Complying | Complying
[11 empty] | 02.02.2026 | 4403 dt. 10.02.2026 | 13.65 | 1: 7.7; 2: 7.8; 3: 44; 5: 16; 11: ND |  |  |  | Complying | Complying
[11 empty] | 02.03.2026 | 4626 dt. 18.03.2026 | 12.02 | 1: 7.98; 2: 8.2; 3: 48; 5: 15; 11: ND |  |  |  | Complying | Complying
[11 empty] | 01.04.2026 | 8 dt 15.04.2026 | 12.3 | 1: 7.1; 2: 8.8; 3: 48; 5: 19; 11: ND |  |  |  | Complying | Complying
[11 empty] | 04.05.2026 | 5 dt 22.05.2026 | 14.8 | 1: 7.3; 2: 8; 3: 44; 5: 17; 11: ND |  |  |  | Complying | Complying
[11 empty] | 02.06.2026 | 98- A dt. 09.06.2026 | 13.1 | 1: 7.6; 2: 9; 3: 46; 5: 18 |  |  |  | Complying | Complying
[11 empty] | 01.07.2026 | 137- A dt. 07.07.2026 | 8.2 | 1: 7.7; 2: 8; 3: 40; 5: 17; 52: BDl (DL=4); 54: 82 |  |  |  | Complying | Complying
| July, 2026 2nd Phase | [9 empty] | 22.07.2026 | HRL/WW-II/2026/215-216-A dt. 04.08.2026 |  | 1: 7.6; 2: 8; 3: 44; 5: 12; 6: 952; 7: 174.9; 8: 342; 9: 132; 18: 92.5; 19: 46; 20: 100; 23: 280; 24: 440; 25: 90; 28: 1.9; 29: 0.6; 30: 1459; 31: 0.4; 52: BDL(DL=4) |  | 0.9 |  | Complying | Complying |  | 7.3 | 98 | 328 |  | 234 | 1658 | 209.9 | 464 | 132 | [8 empty] | 145.5 | 70 | 112 |  |  | 380 | 570 | 4.6X104 |  |  | 2.7 | 2 | 2549 | 0.8 | [20 empty] | 22.6 |  |  |  |  | 1.8
[11 empty] | 05.08.2026 | 275-76-A dt. 18.08.2026 | 8.2 | 1: 8; 2: 8; 3: 40; 5: 14; 6: 642; 7: 104.9; 8: 463.6; 9: 106; 10: 1.1; 13: 1.8; 18: 104.5; 19: 51; 20: 64; 23: 380; 24: 370; 25: 86; 28: 2.4; 29: 0.2; 30: 987; 31: 0.5; 52: BDl (DL=4) |  | 0.8 |  | Complying | Complying | 8.4 | 7.2 | 95 | 320 |  | 226 | 1078 | 229.9 | 646.6 | 215 | 4.4 |  |  | 9.2 |  |  |  |  | 196.5 | 53.4 | 76 |  |  | 530 | 410 | 4.4 X 10⁴ |  |  | 4.2 | 2.4 | 1658 | 0.9 | [20 empty] | 20.4 |  |  |  |  | 1.6
64 | (SRS-STP-004) 7.5 MLD STP Ellenabad Sirsa by PHED in 11.5.2015 (MBBR+TT) |  | 10 | 6.5 to 9 | 50 | 20
[11 empty] | 07.01.2026 | 4256 dt. 20.01.2026 |  | 1: 7.92; 2: 25; 3: 124; 5: 85; 11: 12.59 |  |  |  | non complying | non complying
[11 empty] | 23.02.26 | 4570 dt 10.03.26 |  | 1: 8.2; 2: 5.6; 3: 36; 5: 9; 11: ND; 25: 70; 52: 18.5 |  |  |  | Complying | Complying
[11 empty] | 02.03.26 | 4620 dt. 18.03.26 | 5.1 | 1: 7.8; 2: 7.6; 3: 48; 5: 10; 11: ND; 25: 90; 52: 3.5 |  |  |  | Complying | Complying
[11 empty] | 08.04.26 | 83 dt 24.04.26 | - | 1: 7.54; 2: 7.6; 3: 40; 5: 12; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 04.05.26 | 15-16 dt 22.05.26 | 6.1 | 1: 7.7; 2: 8; 3: 46; 5: 16; 11: ND |  |  |  | Complying | Complying | 6.5 | 7.2 | 105 | 357 |  | 298
[11 empty] | 02.06.2026 | 96- A dt. 09.06.2026 | 6.1 | 1: 7.5; 2: 7; 3: 36; 5: 15 |  |  |  | Complying | Complying
[11 empty] | 01.07.2026 | 133- A dt. 07.07.2026 | 5.5 | 1: 8; 2: 8; 3: 42; 5: 16; 52: BDl (DL=4); 54: 80 |  |  |  | Complying | Complying
| July, 2026 2nd Phase | [9 empty] | 22.07.2026 | HRL/WW-II/2026/225-226-A dt. 04.08.2026 |  | 1: 8; 2: 7; 3: 40; 5: 14; 6: 1238; 7: 184.9; 8: 390; 9: 124; 18: 60.5; 19: 51; 20: 44; 23: 320; 24: 320; 25: 86; 28: 1.5; 29: 0; 30: 1900; 31: 0.3; 52: BDL(DL=4) |  | 0.8 |  | Complying | Complying |  | 7.2 | 103 | 344 |  | 224 | 1604 | 294.9 | 598 | 124 | [8 empty] | 237 | 68 | 56 |  |  | 490 | 420 | 3.9X104 |  |  | 5 | 1.4 | 2458 | 0.9 | [20 empty] | 22.4 |  |  |  |  | 4.1
[11 empty] | 05.08.2026 | 263-64-A dt 18.08.2026 | 5.3 | 1: 8; 2: 8; 3: 40; 5: 16; 6: 1128; 7: 214.9; 8: 866.2; 9: 132; 10: 0.9; 13: 2.1; 16: ND; 18: 108; 19: 87.4; 20: 64; 23: 710; 24: 510; 25: 90; 28: 2; 29: 3.8; 30: 1876; 31: 0.4; 52: BDL(DL=4) |  | 0.9 |  | Complying | Complying | 6.4 | 8.2 | 102 | 340 |  | 238 | 1966 | 429.9 | 1744.6 | 238 | 1.4 |  |  | 8.6 |  |  | 5.6 |  | 562 | 97.2 | 64 |  |  | 1430 | 560 | 4.8 X 10⁴ |  |  | 10.3 | 17.4 | 3024 | 1.1 | [20 empty] | 20.8 |  |  |  |  | 4.3
65 | (SRS-STP-005) 9.5 MLD STP, Daddu Road, Kalanwali , Sirsa by PHED in 17.02.2018 | PHED | 10 | 5.5 to 9 | 100 | 10
[11 empty] | 07.01.2026 | 4249 dt. 20.01.2026 |  | 1: 7.27; 2: 5.8; 3: 40; 5: 13; 11: ND |  |  |  | Complying | Complying
[11 empty] | 09.02.26 | 4462 dt 23.02.26 |  | 1: 7.86; 2: 5.2; 3: 24; 5: 8; 11: ND; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 02.03.26 | 4619 dt 18.03.26 | 3.5 | 1: 7.57; 2: 8.2; 3: 44; 5: 17; 11: ND; 25: 60 |  |  |  | Complying | Complying
[11 empty] | 02.04.26 | 12 dt 15.04.26 | 3.1 | 1: 7.42; 2: 6.8; 3: 40; 5: 7; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 04.05.26 | 10 dt 22.05.26 |  | 1: 7.6; 2: 6; 3: 36; 5: 9; 11: ND; 25: 60 |  |  |  | Complying | Complying
[11 empty] | 02.06.2026 | 104-105- A dt. 09.06.2026 |  | 1: 7.7; 2: 5; 3: 28; 5: 10 |  |  |  | Complying | Complying |  | 7.8 | 92 | 304 |  | 218
[11 empty] | 01.07.2026 | 139-140- A dt. 07.07.2026 | 3 | 1: 7.6; 2: 8; 3: 46; 5: 12; 52: BDL(DL=4); 54: 68 |  |  |  | Complying | Complying | 3.2 | 7.2 | 89 | 296 |  | 226 | [19 empty] | 2.6 X 10⁴
| July, 2026 2nd Phase | [9 empty] | 22.07.2026 | HRL/WW-II/2026/209-210-A dt. 04.08.2026 |  | 1: 7.9; 2: 6; 3: 28; 5: 12; 6: 596; 7: 119.9; 8: 293; 9: 96; 18: 57; 19: 46; 20: 300; 23: 240; 24: 300; 25: 84; 28: 1.4; 29: -1.2; 30: 909; 31: 0.3; 52: BDL(DL=4) |  | 0.8 |  | Complying | Complying |  | 7.7 | 84 | 288 |  | 198 | 1008 | 209.9 | 781 | 180 | [8 empty] | 114 | 49 | 60 |  |  | 640 | 350 | 3.6X104 |  |  | 2.6 | 5.8 | 1547 | 0.6 | [20 empty] | 18.6 |  |  |  |  | 4.2
[11 empty] | 05.08.2026 | 265-66-A dt 18.08.2026 | 3.1 | 1: 7.8; 2: 5; 3: 24; 5: 10; 6: 574; 7: 89.9; 8: 488; 9: 90; 10: 1; 13: 1.2; 16: ND; 18: 54; 19: 34; 20: 84; 23: 400; 24: 350; 25: 80; 28: 1.2; 29: 1; 30: 883; 31: 0.2; 52: BDL(DL=4) |  | 0.6 |  | Complying | Complying | 3.3 | 7.1 | 89 | 396 |  | 202 | 1348 | 329.9 | 658.8 | 184 | 1.3 |  |  | 7.8 |  |  | 3.8 |  | 266 | 36.4 | 108 |  |  | 540 | 420 | 3.9 X 10⁴ |  |  | 5.6 | 2.4 | 2067 | 0.8 | [20 empty] | 22.4 |  |  |  |  | 4.4
66 | (SRS-STP-006) 6 MLD STP Rania Sirsa by PHED in 30.6.2017 | PHED | 10 | 5.5 to 9.0 | 100 | 10
[11 empty] | 07.01.2026 | 4255 dt. 20.01.2026 | 8.58 | 1: 7.64; 2: 18; 3: 92; 5: 28; 11: ND |  |  |  | Complying | Complying
[11 empty] | 02.02.26 | 4402 dt 10.02.26 | 4.67 | 1: 7.24; 2: 7.2; 3: 44; 5: 15; 11: ND |  |  |  | Complying | Complying
[11 empty] | 02.03.26 | 4625 dt 18.03.26 | 4.8 | 1: 7.76; 2: 8; 3: 40; 5: 11; 11: ND; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 01.04.26 | 9 dt 15.04.26 | 5 | 1: 7.13; 2: 8; 3: 40; 5: 15; 11: ND; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 04.05.26 | 9 dt 22.05.26 | 4.8 | 1: 7.3; 2: 7; 3: 44; 5: 15; 11: ND |  |  |  | Complying | Complying
[11 empty] | 02.06.2026 | 97- A dt. 09.06.2026 | 4 | 1: 7.1; 2: 8; 3: 46; 5: 16 |  |  |  | Complying | Complying
[11 empty] | 01.07.2026 | 138- A dt. 07.07.2026 | Not working | 1: 8; 2: 22; 3: 82; 5: 48; 52: (BDL(DDL=4); 54: 1.4X10⁴ |  |  |  | Non complying | Non complying
| July, 2026 2nd Phase | [9 empty] | 22.07.2026 | HRL/WW-II/2026/211-212-A dt. 04.08.2026 |  | 1: 7.8; 2: 8; 3: 48; 5: 16; 6: 784; 7: 194.9; 8: 268; 9: 92; 18: 92; 19: 58; 20: 72; 23: 220; 24: 420; 25: 90; 28: 1.95; 29: -3.97; 30: 1211; 31: 0.4; 52: BDL(DL=4) |  | 0.6 |  | Complying | Complying |  | 7.6 | 95 | 312 |  | 206 | 1126 | 209.9 | 525 | 242 | [8 empty] | 116.5 | 66 | 88 |  |  | 430 | 490 | 3.9X104 |  |  | 2.29 | -1.22 | 1732 | 0.8 | [20 empty] | 18.6 |  |  |  |  | 4.2
[11 empty] | 05.08.2026 | 267-68-A dt 18.08.2026 | Not working | 1: 7.6; 2: 12; 3: 56; 5: 18; 6: 654; 7: 119.9; 8: 378; 9: 95; 10: 1.1; 13: 1.6; 16: ND; 18: 86; 19: 46.1; 20: 68; 23: 310; 24: 360; 25: 1.1X 103; 28: 1.9; 29: -1; 30: 1003; 31: 0.5; 52: (BDL(DDL=4) |  | 0.7 |  | Non complying | Non complying | Not working | 8.1 | 96 | 320 |  | 212 | 1112 | 244.9 | 439 | 236 | 1.2 |  |  | 8.2 |  |  | 4.6 |  | 101 | 48.6 | 72 |  |  | 360 | 380 | 3.7 X 10⁴ |  |  | 2.2 | -0.4 | 1710 | 0.9 | [20 empty] | 18.4 |  |  |  |  | 4.9
67 | (SRS-STP-007) 16.5 MLD STP, Dabwali, Sirsa by PHED in 04.12.2017 |  | 10 | 5.5 to 9 | 100 | 10
[11 empty] | 07.01.2026 | 4250 dt. 20.01.2026 | 3.98 | 1: 7.75; 2: 6.8; 3: 48; 5: 15; 11: ND |  |  |  | Complying | Complying
[11 empty] | 02.02.26 | 4404 dt 10.02.26 | 14.9 | 1: 7.35; 2: 7.8; 3: 48; 5: 15; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 02.03.26 | 4621 dt 18.03.26 | 11.74 | 1: 7.88; 2: 7; 3: 28; 5: 7; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 01.04.26 | 7 dt 15.04.26 | 4.6 | 1: 7.14; 2: 8.2; 3: 44; 5: 16; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 04.05.26 | 17-18 dt 22.05.26 | 12.9 | 1: 7.1; 2: 9; 3: 46; 5: 15; 11: ND |  |  |  | Complying | Complying | 13.6 | 6.8 | 98 | 316 |  | 294
[11 empty] | 02.06.2026 | 101- A dt. 09.06.2026 |  | 1: 7.4; 2: 7; 3: 40; 5: 12 |  |  |  | Complying | Complying
[11 empty] | 01.07.2026 | 134- A dt. 07.07.2026 |  | 1: 8; 2: 8; 3: 32; 5: 12; 52: BDL(DL=4); 54: 68 |  |  |  | Complying | Complying
| July, 2026 2nd Phase | [9 empty] | 22.07.2026 | HRL/WW-II/2026/223-224-A dt. 04.08.2026 |  | 1: 7.7; 2: 9; 3: 44; 5: 16; 6: 584; 7: 74.9; 8: 207; 9: 108; 18: 30; 19: 24; 20: 56; 23: 170; 24: 240; 25: 96; 28: 0.8; 29: -1.4; 30: 895; 31: 0.4; 52: BDL(DL=4) |  | 0.7 |  | Complying | Complying |  | 7.5 | 94 | 312 |  | 220 | 1078 | 194.9 | 464 | 192 | [8 empty] | 120 | 29 | 72 |  |  | 380 | 300 | 3.9X104 |  |  | 3 | 1.6 | 1653 | 1.2 | [20 empty] | 20.4 |  |  |  |  | 4.3
[11 empty] | 05.08.2026 | 261-62-A dt 18.08.2026 | 10.8 | 1: 7.2; 2: 8; 3: 32; 5: 14; 6: 608; 7: 249.9; 8: 500.2; 9: 106; 10: 0.8; 13: 1.4; 16: ND; 18: 68; 19: 48.6; 20: 76; 23: 410; 24: 390; 25: 92; 28: 1.5; 29: 0.4; 30: 934; 31: 0.3; 52: BDL(DL=4) |  | 0.8 |  | Complying | Complying | 11.1 | 7.2 | 92 | 304 |  | 208 | 1218 | 324.9 | 573.4 | 196 | 1.2 |  |  | 8.4 |  |  | 4.2 |  | 250 | 53.4 | 92 |  |  | 470 | 450 | 4.2 X 10⁴ |  |  | 5.1 | -0.4 | 1870 | 1.4 | [20 empty] | 18.2 |  |  |  |  | 4.6
68 | (SRS-STP-008) 20 MLD STP Kelnia, Distt. Sirsa by PHED in 30.10.2019 |  | 10 | 6.5 to 9 | 50 | 20
[11 empty] | 07.01.2026 | 4252 dt. 20.01.2026 | 11 | 1: 7.16; 2: 5.6; 3: 36; 5: 11; 11: ND |  |  |  | Complying | Complying
[11 empty] | 02.02.26 | 4406 dt 10.02.26 | 17.5 | 1: 7.89; 2: 7; 3: 44; 5: 13; 11: ND; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 02.03.26 | 4622 dt 18.03.26 | 15.9 | 1: 7.99; 2: 8.2; 3: 40; 5: 6.5; 11: ND; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 01.04.26 | 10 dt 15.04.26 | 17.5 | 1: 7.17; 2: 7.8; 3: 44; 5: 16; 11: ND; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 04.05.26 | 7 dt 22.05.26 | 18.1 | 1: 7.4; 2: 7; 3: 42; 5: 18; 11: ND |  |  |  | Complying | Complying
[11 empty] | 02.06.2026 | 99- A dt. 09.06.2026 | 14.2 | 1: 7.4; 2: 8; 3: 44; 5: 16 |  |  |  | Complying | Complying
[11 empty] | 01.07.2026 | 131- A dt. 07.07.2026 | 15.4 | 1: 7.6; 2: 7; 3: 40; 5: 12; 52: (BDL(DDL=4); 54: 76 |  |  |  | Complying | Complying
| July, 2026 2nd Phase | [9 empty] | 22.07.2026 | HRL/WW-II/2026/213-214-A dt. 04.08.2026 |  | 1: 7.7; 2: 9; 3: 48; 5: 18; 6: 1028; 7: 139.9; 8: 256; 9: 98; 18: 100; 19: 41; 20: 60; 23: 210; 24: 320; 25: 92; 28: 2.44; 29: -2.1; 30: 1580; 31: 0.3; 52: BDL(DL=4) |  | 0.7 |  | Complying | Complying |  | 6.6 | 82 | 272 |  | 194 | 1278 | 184.9 | 329 | 210 | [8 empty] | 276 | 49 | 68 |  |  | 270 | 370 | 4.3X104 |  |  | 6.23 | -2 | 1962 | 0.5 | [20 empty] | 18.4 |  |  |  |  | 1.2
[11 empty] | 05.08.2026 | 271-72-A dt 18.08.2026 | 15.4 | 1: 7.6; 2: 9; 3: 48; 5: 16; 6: 1054; 7: 234.9; 8: 402.6; 9: 102; 10: 1.2; 13: 1.6; 16: ND; 18: 104; 19: 41.3; 20: 60; 23: 330; 24: 320; 25: 96; 28: 2.5; 29: 0.2; 30: 1617; 31: 0.4; 52: (BDL(DDL=4) |  | 0.8 |  | Complying | Complying | 15.6 | 7 | 86 | 288 |  | 220 | 1698 | 319.9 | 658.8 | 218 | 1.3 |  |  | 9.6 |  |  |  |  | 219 | 53.4 | 72 |  |  | 540 | 400 | 4.5 X 10⁴ |  |  | 4.7 | 2.8 | 2458 | 0.8 | [20 empty] | 20.6 |  |  |  |  | 1.4
69 | (SRS-STP-009) 7.5 MLD STP, Vaidwala Sirsa by HSVP in 31.01.2022
[11 empty] | 07.01.2026 | 4254 dt. 20.01.2026 | 1.52 | 1: 7.29; 2: 7.5; 3: 44; 5: 13; 11: ND |  |  |  | Complying | Complying
[11 empty] | 02.02.26 | 4405 dt 10.02.26 | 1.7 | 1: 7.15; 2: 5.8; 3: 32; 5: 9; 11: ND; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 02.03.26 | 4623 dt 18.03.26 | 5.6 | 1: 7.75; 2: 8.6; 3: 36; 5: 12; 11: ND; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 01.04.26 | 6 dt 15.04.26 | 3.2 | 1: 7.83; 2: 8.5; 3: 48; 5: 17; 11: ND; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 04.05.26 | 8 dt 22.05.26 | 1.7 | 1: 7.5; 2: 8; 3: 42; 5: 16; 11: ND; 25: 80 |  |  |  | Complying | Complying
[11 empty] | 02.06.2026 | 95- A dt. 09.06.2026 | 6.6 | 1: 7.2; 2: 8; 3: 40; 5: 14 |  |  |  | Complying | Complying
[11 empty] | 01.07.2026 | 132- A dt. 07.07.2026 | 5.9 | 1: 8; 2: 6; 3: 32; 5: 10; 52: BDL(DL=4); 54: 72 |  |  |  | Complying | Complying
| July, 2026 2nd Phase | [9 empty] | 22.07.2026 | HRL/WW-II/2026/219-220-A dt. 04.08.2026 |  | 1: 7.9; 2: 7; 3: 32; 5: 14; 6: 1254; 7: 99.9; 8: 342; 9: 154; 18: 81.5; 19: 22; 20: 36; 23: 280; 24: 180; 25: 92; 28: 2.6; 29: 2; 30: 1923; 31: 0.4; 52: BDL(DL=4) |  | 0.7 |  | Complying | Complying |  | 7.4 | 92 | 304 |  | 208 | 1378 | 139.9 | 366 | 218 | [8 empty] | 62.5 | 17 | 72 |  |  | 300 | 250 | 4.2X104 |  |  | 1.7 | -1.01 | 2116 | 0.9 | [20 empty] | 18.2 |  |  |  |  | 4.8
[11 empty] | 05.08.2026 | 273-74-A dt 18.08.2026 | 5.9 | 1: 7.9; 2: 7; 3: 32; 5: 10; 6: 618; 7: 124.9; 8: 341.6; 9: 118; 10: 1; 13: 1.2; 17: ND; 18: 86; 19: 19.4; 20: 60; 23: 280; 24: 230; 25: 82; 28: 2.4; 29: 1; 30: 949; 31: 0.3; 52: BDL(DL=4) |  | 0.7 |  | Complying | Complying | 6 | 7.5 | 83 | 276 |  | 204 | 694 | 199.9 | 427 | 232 | 1.1 |  |  | 8 |  |  |  |  | 124 | 24.3 | 68 |  |  | 350 | 270 | 4.2 X 10⁴ |  |  | 3.2 | 1.6 | 1014 | 0.6 | [20 empty] | 18.8 |  |  |  |  | 1.6
70 | (SRS-STP-010) 12.5 MLD STP, Nattar, Sirsa by
[11 empty] | 07.01.2026 | 4251 dt. 20.01.2026 | 10.2 | 1: 7.2; 2: 7.2; 3: 48; 5: 16; 11: ND |  |  |  | Complying | Complying
[11 empty] | 02.02.26 | 4408 dt 10.02.26 | 10.8 | 1: 7.84; 2: 6.8; 3: 40; 5: 12; 11: ND; 25: 60 |  |  |  | Complying | Complying
[11 empty] | 02.03.26 | 4624 dt 18.03.26 | 10.9 | 1: 7.84; 2: 8.8; 3: 44; 5: 13; 11: ND; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 01.04.26 | 5 dt 15.04.26 | 10.7 | 1: 7; 2: 8.6; 3: 48; 5: 18; 11: ND; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 04.05.26 | 6 dt 22.05.26 | 10.6 | 1: 7.1; 2: 8; 3: 46; 5: 16; 11: ND; 25: 86 |  |  |  | Complying | Complying
[11 empty] | 02.06.2026 | 100- A dt. 09.06.2026 | 11 | 1: 7.3; 2: 8; 3: 42; 5: 14 |  |  |  | Complying | Complying
[11 empty] | 01.07.2026 | 130- A dt. 07.07.2026 | 10 | 1: 6.9; 2: 9; 3: 44; 5: 16; 52: (BDL(DL=4); 54: 92 |  |  |  | Complying | Complying
| July, 2026 2nd Phase | [9 empty] | 22.07.2026 | HRL/WW-II/2026/217-218-A dt. 04.08.2026 |  | 1: 7.8; 2: 7; 3: 40; 5: 16; 6: 1286; 7: 179.9; 8: 451; 9: 174; 18: 82; 19: 66; 20: 84; 23: 370; 24: 480; 25: 86; 28: 1.6; 29: -2.2; 30: 1968; 31: 0.6; 52: BDL(DL=4) |  | 1.3 |  | Complying | Complying |  | 7.3 | 95 | 316 |  | 228 | 1830 | 299.9 | 586 | 268 | [8 empty] | 218 | 100 | 124 |  |  | 480 | 720 | 4.6X104 |  |  | 3.5 | -4.8 | 2810 | 1.1 | [20 empty] | 20.8 |  |  |  |  | 5.1
[11 empty] | 05.08.2026 | 279-80-A dt 18.08.2026 | 10 | 1: 7.8; 2: 7; 3: 32; 5: 14; 6: 568; 7: 89.9; 8: 500.2; 9: 142; 10: 1.2; 13: 1.8; 16: ND; 18: 91; 19: 43.7; 20: 68; 23: 410; 24: 350; 25: 82; 28: 2.1; 29: 1.2; 30: 868; 31: 0.4; 52: (BDL(DL=4) |  | 1 |  | Complying | Complying | 10.2 | 7.1 | 91 | 304 |  | 234 | 1106 | 234.9 | 658.8 | 236 | 1.3 |  |  | 8.5 |  |  |  |  | 220 | 48.6 | 76 |  |  | 540 | 390 | 4.3 X 10⁴ |  |  | 4.8 | 3 | 1700 | 0.9 | [20 empty] | 22.8 |  |  |  |  | 4.6
Fatehabad
71 | (FTB-STP-001) 10 MLD STP Vill. Bhodia Khera, Bhattu Road , Fatehabad by PHED in 1.4.2013 |  | 10 | 6.5 to 9 | 50 | 20
[11 empty] | 07.01.2026 | 4245 dt. 20.01.2026 | 7.2 | 1: 2.4; 2: 3.8; 3: 32; 5: 13; 11: 3.22 |  |  |  | Complying | Complying | 7.3 | 6.93 | 120 | 388 |  | 178 | [5 empty] | 14.24
[11 empty] | 10.02.2026 | 4458 dt. 23.02.2026 | 7.76 | 1: 7.6; 2: 7.8; 3: 44; 5: 15; 11: 4.28; 25: 50 |  |  |  | Complying | Complying |  | 7.33 | 125 | 408 |  | 210 | [5 empty] | 14.72
[11 empty] | 10.03.2026 | 4671 dt. 24.03.2026 |  | 1: 7.92; 2: 7.4; 3: 48; 5: 7; 11: BDL; 25: 50 |  |  |  | Complying | Complying |  | 7.04 | 135 | 396 |  | 304 | [5 empty] | 15.38 | [13 empty] | -
[11 empty] | 03.04.2026 | 17 dt. 15.04.2026 |  | 1: 7.03; 2: 7.8; 3: 44; 5: 13; 11: 1.84; 25: 70 |  |  |  | Complying | Complying |  | 6.98 | 140 | 508 |  | 295 | [5 empty] | 19.35 | [13 empty] | -
[11 empty] | 06.05.2026 | HRL/WW-II/2026/29-30 dt. 22.05.2026 |  | 1: 7.3; 2: 7; 3: 18; 5: 12 |  |  |  | Complying | Complying |  | 6.8 | 149 | 544 |  | 318
[11 empty] | 02.06.2026 | HRL/WW-II/2026/85-86-A dt. 09.06.2026 |  | 1: 7.4; 2: 8; 3: 28; 5: 13 |  |  |  | Complying | Complying |  | 6.9 | 127 | 456 |  | 304
[11 empty] | 01.07.2026 | HRL/WW-II/2026/149-150-A dt. 07.07.2026 |  | 1: 7.2; 2: 38; 3: 144; 5: 86; 25: 2.2 X104; 52: 6.2; 55: 1202 |  |  |  | Non complying | Non complying |  | 6.9 | 114 | 432 |  | 318 | [19 empty] | 1.3 X 105 | [26 empty] | 18.2 |  |  | 1330
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | HRL/WW-II/2026/205-206-A dt. 30.07.2026 |  | 1: 7.5; 2: 22; 3: 72; 5: 68; 6: 762; 7: 334.9; 8: 390; 9: 48; 18: 89.2; 19: 19; 20: 230; 23: 320; 24: 230; 25: 2.6 X104; 28: 2.6; 29: 0.6; 30: 1170; 31: 0.3; 52: 5.8 |  | 0.7 |  | Non complying | Non complying |  | 7.2 | 82 | 272 |  | 184 | 904 | 339.9 | 476 | 62 | [8 empty] | 103 | 22 | 36 |  |  | 390 | 280 | 3.9X104 |  |  | 2.6 | 1 | 1389 | 0.5 | [20 empty] | 18.4 |  |  |  |  | 1.2
[11 empty] | 03.08.2026 | HRL/WW-II/2026/237-238-A dt. 10.08.2026 |  | 1: 7; 2: 24; 3: 76; 5: 62; 52: 6.2; 54: 2.6X103; 55: 1062 |  |  |  | Non complying | Non complying |  | 6.8 | 90 | 304 |  | 208 | [46 empty] | 14.4 |  | 2.1X105 | 1200
72 | (FTB-STP-002) 10 MLD STP Vill.Amani, Tohana, Distt. Fatehabad by PHED in 1.4.2013 |  | 20 | 6.5 to 9 | 50 | 20
[11 empty] | 07.01.2026 | 4242 dt. 20.01.2026 | 5.6 | 1: 7.13; 2: 7.2; 3: 48; 5: 14; 11: 1.68 |  |  |  | Complying | Complying | - | 7.06 | 135 | 460 |  | 264 | [5 empty] | 14.88
[11 empty] | 10.02.2026 | 4460 dt. 23.02.2026 | 7.4 | 1: 7.73; 2: 7; 3: 48; 5: 15; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 7 | 130 | 432 |  | 218 | [5 empty] | 15.23 | [13 empty] | -
[11 empty] | 10.03.2026 | 4669 dt. 24.03.2026 | 7.6 | 1: 7.98; 2: 5.4; 3: 36; 5: 13; 11: BDL; 25: 70 |  |  |  | Complying | Complying | - | 6.94 | 140 | 456 |  | 326 | [5 empty] | 14.78 | [13 empty] | -
[11 empty] | 03.04.2026 | 13 dt. 15.04.2026 | 8.1 | 1: 7.44; 2: 7.2; 3: 44; 5: 15; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 7.2 | 120 | 408 |  | 294 | [5 empty] | 17.86 | [13 empty] | -
[11 empty] | 06.05.2026 | HRL/WW-II/2026/23-24 dt. 22.05.2026 | 8.5 | 1: 7.4; 2: 8; 3: 46; 5: 17 |  |  |  | Complying | Complying |  | 6.9 | 108 | 340 |  | 226
[11 empty] | 02.06.2026 | HRL/WW-II/2026/91-92-A dt. 09.06.2026 | 7.4 | 1: 7.1; 2: 7; 3: 32; 5: 14 |  |  |  | Complying | Complying | - | 6.7 | 92 | 304 |  | 215
[11 empty] | 01.07.2026 | HRL/WW-II/2026/141-142-A dt. 07.07.2026 | 258.5 | 1: 7.5; 2: 6; 3: 32; 5: 12; 25: 72; 52: (BDL(DL=4); 55: 649 |  |  |  | Complying | Complying | - | 6.9 | 95 | 312 |  | 242 | [19 empty] | 2.5 X 104 | [26 empty] | 16.4 |  |  | 1858
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | HRL/WW-II/2026/207-208-A dt. 30.07.2026 |  | 1: 7.6; 2: 8; 3: 40; 5: 12; 6: 306; 7: 84.9; 8: 122; 9: 18; 18: 30.4; 19: 19; 20: 180; 23: 100; 24: 180; 25: 86; 28: 0.5; 29: -1.6; 30: 463; 31: 0.1; 52: BDL(DL=4) |  | 0.3 |  | Complying | Complying |  | 7.7 | 68 | 224 |  | 196 | 604 | 149.9 | 354 | 42 | [8 empty] | 63 | 34 | 60 |  |  | 290 | 290 | 3.1X104 |  |  | 1.7 | 1 | 924 | 0.3 | [20 empty] | 14.8 |  |  |  |  | 0.8
[11 empty] | 03.08.2026 | HRL/WW-II/2026/241-242-A dt. 10.08.2026 |  | 1: 7.3; 2: 5; 3: 16; 5: 9; 52: BDL(DL=4); 54: 58; 55: 343 |  |  |  | Complying | Complying |  | 6.9 | 78 | 264 |  | 174 | [46 empty] | 14.2 |  | 2.8X104 | 916
73 | (FTB-STP-003) 6.5 MLD STP Ratia , Fatehabad by PHED in 1.9.2014 (MBBR) |  | 10 | 6.5 to 9 | 50 | 20
[11 empty] | 07.01.2026 | 4244 dt. 20.01.2026 |  | 1: 7.34; 2: 6.5; 3: 40; 5: 13; 11: 4.68 |  |  |  | Complying | Complying |  | 7.01 | 130 | 480 |  | 292 | [5 empty] | 16.24
[11 empty] | 10.02.2026 | 4456 dt. 23.02.2026 |  | 1: 7.7; 2: 8; 3: 48; 5: 17; 11: 3.52; 25: 80 |  |  |  | Complying | Complying |  | 7.16 | 120 | 392 |  | 220 | [5 empty] | 14.35 | [13 empty] | -
[11 empty] | 10.03.2026 | 4674 dt. 24.03.2026 | 5.85 | 1: 7.92; 2: 7.5; 3: 40; 5: 12; 11: BDL; 25: 90 |  |  |  | Complying | Complying |  | 7.09 | 170 | 572 |  | 284 | [5 empty] | 12.98 | [13 empty] | -
[11 empty] | 03.04.2026 | 18 dt. 15.04.2026 |  | 1: 7.53; 2: 8.2; 3: 44; 5: 14; 11: 2.86; 25: 90 |  |  |  | Complying | Complying |  | 7.05 | 120 | 396 |  | 196 | [5 empty] | 14.37
[11 empty] | 06.05.2026 | HRL/WW-II/2026/31-32 dt.22.05.2026 | 5.97 | 1: 7; 2: 7; 3: 40; 5: 12 |  |  |  | Complying | Complying | - | 7.7 | 112 | 285 |  | 218
[11 empty] | 02.06.2026 | HRL/WW-II/2026/89-90-A dt. 09.06.2026 | 5.9 | 1: 7.3; 2: 6; 3: 28; 5: 10 |  |  |  | Complying | Complying |  | 7.2 | 82 | 272 |  | 208
[11 empty] | 02.07.2026 | HRL/WW-II/2026/153-154-A dt. 07.07.2026 | 5.95 | 1: 7.5; 2: 5; 3: 24; 5: 8; 25: 64; 52: BDL(DL=4); 55: 420 |  |  |  | Complying | Complying | - | 7.3 | 96 | 312 |  | 234 | [19 empty] | 1.8 X104 | [26 empty] | 20.8
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | HRL/WW-II/2026/201-202-A dt. 30.07.2026 |  | 1: 7.7; 2: 9; 3: 44; 5: 15; 6: 340; 7: 109.9; 8: 146; 9: 30; 18: 38; 19: 17; 20: 200; 23: 120; 24: 200; 25: 90; 28: 1.3; 29: -2.2; 30: 517; 31: 0.1; 52: BDL(DL=4) |  | 0.4 |  | Complying | Complying |  | 7.9 | 65 | 256 |  | 204 | 868 | 189.9 | 512 | 74 | [8 empty] | 123.4 | 34 | 48 |  |  | 420 | 260 | 3.4X104 |  |  | 2.8 | 3.4 | 1333 | 0.4 | [20 empty] | 20.4 |  |  |  |  | 2.3
[11 empty] | 03.08.2026 | HRL/WW-II/2026/229-230-A dt. 10.08.2026 |  | 1: 8; 2: 5; 3: 20; 5: 10; 52: BDL(DL=4); 54: 68; 55: 1019 |  |  |  | Complying | Complying |  | 6.9 | 86 | 284 |  | 178 | [46 empty] | 16.4 |  | 3.2X104 | 1246
74 | (FTB-STP-004) 10 MLD STP Majra, Fatehabad by HUDA in 16.12.17
[11 empty] | 07.01.2026 | 4246 dt. 20.01.2026 | 581 | 1: 7.34; 2: 7.2; 3: 48; 5: 15; 11: 1.76 |  |  |  | Complying | Complying | 594 | 6.7 | 145 | 520 |  | 388 | [5 empty] | 14.58
[11 empty] | 10.02.2026 | 4455 dt. 23.02.2026 |  | 1: 7.77; 2: 7.8; 3: 44; 5: 13; 11: 2.74; 25: 90 |  |  |  | Complying | Complying |  | 7.1 | 110 | 380 |  | 148 | [5 empty] | 18.23 | [13 empty] | -
[11 empty] | 10.03.2026 | 4673 dt. 24.03.2026 |  | 1: 7.69; 2: 7.2; 3: 40; 5: 8; 11: BDL; 25: 70 |  |  |  | Complying | Complying |  | 7.16 | 130 | 376 |  | 204 | [5 empty] | 13.25 | [13 empty] | -
[11 empty] | 03.04.2026 | 19 dt. 15.04.2026 |  | 1: 7.7; 2: 5.2; 3: 28; 5: 7; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 6.96 | 135 | 492 |  | 208 | [5 empty] | 15.48 | [13 empty] | -
[11 empty] | 06.05.2026 | HRL/WW-II/2026/21-22 dt. 22.05.2026 |  | 1: 7.7; 2: 6; 3: 37; 5: 10 |  |  |  | Complying | Complying |  | 7.3 | 138 | 499 |  | 248
[11 empty] | 02.06.2026 | HRL/WW-II/2026/83-84-A dt. 09.06.2026 | 0.6 | 1: 8; 2: 7; 3: 32; 5: 14 |  |  |  | Complying | Complying | - | 7 | 113 | 384 |  | 254
[11 empty] | 01.07.2026 | HRL/WW-II/2026/145-146-A dt. 07.07.2026 | 0.7 | 1: 7.7; 2: 5; 3: 28; 5: 12; 25: 70; 52: BDL(DL=4) |  |  |  | Complying | Complying | - | 7.3 | 107 | 352 |  | 268 | [19 empty] | 2.3 X104 | [26 empty] | 18.4
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | HRL/WW-II/2026/203-204-A dt. 30.07.2026 |  | 1: 8.4; 2: 17; 3: 68; 5: 32; 6: 586; 7: 199.9; 8: 158; 9: 26; 18: 109.4; 19: 19; 20: 150; 23: 130; 24: 150; 25: 1.8 X103; 28: 3.9; 29: -0.4; 30: 891; 31: 0.2; 52: BDL(DL=4) |  | 0.4 |  | Non complying | Non complying |  | 7.8 | 86 | 296 |  | 178 | 978 | 244.9 | 549 | 68 | [8 empty] | 129.2 | 27 | 64 |  |  | 450 | 270 | 3.5X104 |  |  | 3.4 | 3.6 | 1503 | 0.6 | [20 empty] | 16.4 |  |  |  |  | 1.4
[11 empty] | 03.08.2026 | HRL/WW-II/2026/233-234-A dt. 10.08.2026 |  | 1: 7.7; 2: 5; 3: 20; 5: 8; 52: BDL(DL=4); 54: 64; 55: 1062 |  |  |  | Complying | Complying |  | 7.4 | 82 | 272 |  | 176 | [46 empty] | 14.8 |  | 3.6X104 | 1274
75 | (FTB-STP-005) 5 MLD STP Kharati Khera Road, Fatehabad by PHED in 31.10.2018 | PHED | 10 | 6.5 to 9 | 50 | 20
[11 empty] | 07.01.2026 | 4243 dt. 20.01.2026 | 3.3 | 1: 7.13; 2: 6.8; 3: 44; 5: 16; 11: 2.08 |  |  |  | Complying | Complying | 3.4 | 7 | 108 | 396 |  | 244 | [5 empty] | 13.94
[11 empty] | 10.02.2026 | 4457 dt. 23.02.2026 |  | 1: 7.65; 2: 6.8; 3: 40; 5: 10; 11: ND; 25: 70 |  |  |  | Complying | Complying |  | 6.85 | 102 | 356 |  | 144 | [5 empty] | 12.84 | [13 empty] | -
[11 empty] | 10.03.2026 | 4672 dt. 24.03.2026 |  | 1: 7.94; 2: 7.8; 3: 44; 5: 11; 11: BDL; 25: 50 |  |  |  | Complying | Complying |  | 6.79 | 120 | 376 |  | 232 | [5 empty] | 17.28 | [13 empty] | -
[11 empty] | 03.04.2026 | 16 dt. 15.04.2026 |  | 1: 7.36; 2: 5.8; 3: 32; 5: 11; 11: ND; 25: 80 |  |  |  | Complying | Complying |  | 7.29 | 140 | 488 |  | 238 | [5 empty] | 16.72 | [13 empty] | -
[11 empty] | 06.05.2026 | HRL/WW-II/2026/25-26 dt. 22.05.2026 |  | 1: 7.3; 2: 17; 3: 62; 5: 48 |  |  |  | Non complying | Non complying |  | 6.9 | 124 | 418 |  | 216
[11 empty] | 02.06.2026 | HRL/WW-II/2026/87-88-A dt. 09.06.2026 |  | 1: 7.2; 2: 19; 3: 66; 5: 46 |  |  |  | Non complying | Non complying |  | 6.6 | 129 | 450 |  | 232
[11 empty] | 01.07.2026 | HRL/WW-II/2026/147-148-A dt. 07.07.2026 |  | 1: 7.3; 2: 7; 3: 28; 5: 12; 25: 78; 52: BDL(DL=4); 55: 658 |  |  |  | Complying | Complying |  | 6.8 | 125 | 424 |  | 208 | [19 empty] | 2.3 X104 | [26 empty] | 18.4 |  |  | 1253
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | HRL/WW-II/2026/197-198-A dt. 30.07.2026 |  | 1: 7.5; 2: 6; 3: 28; 5: 10; 6: 364; 7: 79.9; 8: 73; 9: 28; 18: 31.4; 19: 27; 20: 210; 23: 60; 24: 210; 25: 76; 28: 0.9; 29: -3; 30: 558; 31: 0.1; 52: BDL(DL=4) |  | 2.8 |  | Complying | Complying |  | 6.9 | 114 | 456 |  | 196 | 718 | 204.9 | 378 | 58 | [8 empty] | 77.4 | 39 | 60 |  |  | 310 | 310 | 3.8X104 |  |  | 1.9 | 0 | 1098 | 0.3 | [20 empty] | 18.4 |  |  |  |  | 2.8
[11 empty] | 03.08.2026 | HRL/WW-II/2026/235-236-A dt. 10.08.2026 |  | 1: 7.4; 2: 6; 3: 20; 5: 12; 52: BDL(DL=4); 54: 56; 55: 458 |  |  |  | Complying | Complying |  | 6.8 | 84 | 276 |  | 168 | [46 empty] | 18.8 |  | 3.8X104 | 1187
76 | (FTB-STP-006) 3 MLD STPJhakhal Mandi, Kasimpur Road, Fatehabad by PHED in 31.12.2019 | PHED | 10 | 6.5 to 9 | 50 | 20
[11 empty] | 07.01.2026 | 4247 dt. 20.01.2026 |  | 1: 7.39; 2: 15; 3: 76; 5: 24; 11: 7.28 |  |  |  | Non complying | Non complying |  | 7.36 | 110 | 416 |  | 266 | [5 empty] | 17.28
[11 empty] | 10.02.2026 | 4460 dt. 23.02.2026 | 2.5 | 1: 7.84; 2: 16; 3: 84; 5: 34; 11: 8.94; 25: 400 |  |  |  | Non complying | Non complying |  | 7.3 | 135 | 452 |  | 237 | [5 empty] | 17.32 | [13 empty] | -
[11 empty] | 10.03.2026 | 4668 dt. 24.03.2026 | 2.5 | 1: 8.04; 2: 22; 3: 124; 5: 26; 11: BDL; 25: 400 |  |  |  | Non complying | Non complying |  | 7.84 | 130 | 384 |  | 110 | [5 empty] | 12.46 | [13 empty] | -
[11 empty] | 03.04.2026 | 15 dt. 15.04.2026 | 2.5 | 1: 7.83; 2: 21; 3: 96; 5: 34; 11: 7.28; 25: 600 |  |  |  | Non complying | Non complying |  | 7.4 | 240 | 832 |  | 704 | [5 empty] | 17.78 | [13 empty] | -
[11 empty] | 06.05.2026 | HRL/WW-II/2026/27-28 dt. 22.05.2026 | 2.5 | 1: 7.4; 2: 23; 3: 108; 5: 42 |  |  |  | Non complying | Non complying | - | 7.3 | 96 | 325 |  | 418
[11 empty] | 02.05.2026 | HRL/WW-II/2026/81-82-A dt. 09.06.2026 | 1.25 | 1: 7.4; 2: 25; 3: 94; 5: 48 |  |  |  | Non complying | Non complying | - | 7.1 | 118 | 464 |  | 392 | [19 empty] | 2.9 X 10⁴
[11 empty] | 02.06.2026 | HRL/WW-II/2026/81-82-A dt. 09.06.2026 | 1.25 | 1: 7.4; 2: 25; 3: 94; 5: 48 |  |  |  | Non complying | Non complying | - | 7.1 | 118 | 464 |  | 392
[11 empty] | 02.07.2026 | HRL/WW-II/2026/151-152-A dt. 07.07.2026 | 2.5 | 1: 7.2; 2: 24; 3: 96; 5: 62; 25: 1.8X104; 52: 5.2; 55: 1530 |  |  |  | Non complying | Non complying | - | 7.2 | 109 | 408 |  | 356 | [19 empty] | 3.2 X 104
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | HRL/WW-II/2026/199-200-A dt. 30.07.2026 |  | 1: 8.4; 2: 39; 3: 132; 5: 68; 6: 1028; 7: 184.9; 8: 781; 9: 82; 18: 178; 19: 32; 20: 230; 23: 640; 24: 230; 25: 1.9X104; 28: 2.3; 29: 6.3; 30: 1581; 31: 0.4; 52: 5.8 |  | 2.6 |  | Non complying | Non complying |  | 7.6 | 70 | 232 |  | 158 | 1074 | 199.9 | 744 | 88 | [8 empty] | 189 | 53 | 44 |  |  | 610 | 330 | 2.8X104 |  |  | 2.2 | 5.3 | 1651 | 0.5 | [20 empty] | 18.8 |  |  |  |  | 2.9
[11 empty] | 03.08.2026 | HRL/WW-II/2026/231-232-A dt. 10.08.2026 |  | 1: 7.5; 2: 36; 3: 140; 5: 84; 52: 6.8; 54: 2.1X103; 55: 1668 |  |  |  | Non complying | Non complying |  | 7.6 | 89 | 296 |  | 182 | [46 empty] | 18.2 |  | 3.9X104 | 1668
77 | (FTB-STP-007) 8 MLD STP at Bhuna, Fatehabad by PHED dt. 30.06.2021
[11 empty] | 07.01.2026 | 4248 dt. 20.01.2026 |  | 1: 7.29; 2: 7; 3: 44; 5: 13; 11: ND |  |  |  | Complying | Complying |  | 6.99 | 120 | 396 |  | 245 | [5 empty] | 15.68
[11 empty] | 10.02.2026 | 4459 dt. 23.02.2026 | 1.7 | 1: 7.56; 2: 5.6; 3: 36; 5: 9; 11: ND; 25: 70 |  |  |  | Complying | Complying |  | 6.84 | 120 | 420 |  | 188 | [5 empty] | 14.25 | [13 empty] | -
[11 empty] | 10.03.2026 | 4670 dt. 24.03.2026 | 2.6 | 1: 7.79; 2: 5.2; 3: 32; 5: 6; 11: BDL; 25: 50 |  |  |  | Complying | Complying | - | 7.52 | 150 | 440 |  | 272 | [5 empty] | 14.92 | [13 empty] | -
[11 empty] | 03.04.2026 | 14 dt. 15.04.2026 | 1.2 | 1: 7.37; 2: 8.6; 3: 48; 5: 17; 11: BDL; 25: 80 |  |  |  | Complying | Complying | - | 7.29 | 125 | 412 |  | 318 | [5 empty] | 18.76 | [13 empty] | -
[11 empty] | 06.05.2026 | HRL/WW-II/2026/19-20 dt. 22.05.2026 | 2.7 | 1: 7.2; 2: 8; 3: 40; 5: 16 |  |  |  | Complying | Complying |  | 6.9 | 120 | 407 |  | 306
[11 empty] | 02.06.2026 | HRL/WW-II/2026/93-94-A dt. 09.06.2026 | 2.1 | 1: 7.2; 2: 7; 3: 28; 5: 12 |  |  |  | Complying | Complying | - | 6.8 | 134 | 496 |  | 322
| July, 2026 1st Phase | [9 empty] | 01.07.2026 | HRL/WW-II/2026/143-144-A dt. 07.07.2026 | 2.1 | 1: 7.5; 2: 8; 3: 40; 5: 14; 25: 76; 52: BDL(DL=4) |  |  |  | Complying | Complying | - | 7.1 | 126 | 432 |  | 298 | [19 empty] | 1.1 X 105 | [26 empty] | 20.8 |  |  | 1320
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | HRL/WW-II/2026/195-196-A dt. 30.07.2026 |  | 1: 7.3; 2: 7; 3: 40; 5: 10; 6: 382; 7: 119.9; 8: 122; 9: 35; 18: 38; 19: 29; 20: 220; 23: 100; 24: 220; 25: 92; 28: 1.1; 29: -2.4; 30: 588; 31: 0.2; 52: BDL(DL=4) |  | 0.4 |  | Complying | Complying |  | 6.9 | 114 | 456 |  | 196 | 718 | 204.9 | 378 | 58 | [8 empty] | 77.4 | 39 | 60 |  |  | 310 | 310 | 3.8X104 |  |  | 1.9 | 0 | 1098 | 0.3 | [20 empty] | 18.4 |  |  |  |  | 2.8
[11 empty] | 03.08.2026 | HRL/WW-II/2026/239-240-A dt. 10.08.2026 |  | 1: 7.4; 2: 4; 3: 12; 5: 8; 52: BDL(DL=4); 54: 56; 55: 524 |  |  |  | Complying | Complying |  | 6.9 | 80 | 272 |  | 154 | [46 empty] | 16.8 |  |  | 1692
Yamuna Nagar
78 | 03 MLD STP, PHED, Sadhaura, Yamunanagar
[11 empty] | 25.02.2026 | 4586 dt. 10.03.2026 |  | 1: 7.96; 2: 6.5; 3: 40; 5: 12; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 14.03.2026 | 4718 dt. 01.04.2026 | 36594.6 | 1: 7.49; 2: 3.8; 3: 20; 5: 8; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 07.04.2026 | 53 dt. 22.04.2026 |  | 1: 7.09; 2: 6.8; 3: 36; 5: 13; 11: ND; 25: 60 |  |  |  | Complying | Complying
[11 empty] | 19.05.2026 | 285 dt. 01.06.2026 |  | 1: 7.82; 2: 13; 3: 52; 5: 24; 11: 16.812; 25: 90 |  |  |  | Non-complying | Non-complying
[11 empty] | 10.06.2026 | 490 dt. 23.06.2026 | 29152.68 | 1: 8.24; 2: 8; 3: 44; 5: 9; 11: BDL; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 03.07.2026 | 579 dt. 10.07.2026 | 32186.71 | 1: 7.47; 2: 5.2; 3: 24; 5: 7; 11: ND; 15: 0.47; 25: ND; 52: BDL(DL=02); 55: 547 |  |  |  | Complying | Complying | [52 empty] | 32.5 |  |  | 1442
Other Catchment
Bhiwani/ Charkhi Dadri
1 | (BHI-STP-001) 10 MLD STP Dhana Road , Bhiwani Phase-I by PHED in 16.6.2013 (MBBR) |  | 20 | 6.5-8.0 | 100 | 40
[11 empty] | 14.01.2026 | 2041 dt. 29.01.2026 |  | 1: 7.29; 2: 88; 3: 352; 5: 168; 11: 13.81; 25: 840 |  |  |  | Non complying | Non complying
[11 empty] | 05.02.2026 | 2265 dt. 13.02.2026 |  | 1: 6.85; 2: 92; 3: 387.07; 5: 140; 11: 18.01; 25: 3300 |  |  |  | Non complying | Non complying
[11 empty] | 27.03.2026 | 2697 dt. 07.04.2026 |  | 1: 6.11; 2: 98; 3: 408; 5: 185; 11: 28.02; 25: 6300 |  |  |  | Non complying | Non complying
[11 empty] | 13.04.2026 | 118 dt. 23.04.2026 |  | 1: 7.03; 2: 105; 3: 395.1; 5: 205; 11: 30.14; 25: 7900 |  |  |  | Non complying | Non complying
[11 empty] | 14.05.2026 | HRL/WW-I/2026/127-128-A dt. 20.05.2026 |  | 1: 7.8; 2: 12; 3: 56; 5: 17; 11: 12.4; 25: 210 |  |  |  | Non complying | Non complying |  | 8.8 | 142 | 504 |  | 422 | [5 empty] | 32.2 | [13 empty] | 8.6X10⁴
[11 empty] | 03.06.2026 | HRL/WW-I/2026/270-271-A dt. 08.06.2026 |  | 1: 7.6; 2: 14; 3: 104; 5: 18; 11: 12.8; 25: 72 |  |  |  | Non complying | Non complying |  | 8.6 | 132 | 456 |  | 396 | [5 empty] | 28.4 | [13 empty] | 2.8X10⁴
| July, 2026 1st Phase | [9 empty] | 07.07.2026 | HRL/WW-I/2026/429-430-A dt. 14.07.2026 |  | 1: 7.5; 2: 90; 3: 230; 5: 256; 11: 18; 25: 380 |  |  |  | Non complying | Non complying |  | 8.2 | 146 | 472 |  | 348 | [5 empty] | 34 | [13 empty] | 3.2X10⁴ | [26 empty] | 28
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | HRL/WW-I/2026/534-535-A dt. 30.07.2026 |  | 1: 8; 2: 82; 3: 128; 5: 78; 6: 742; 7: 291.1; 8: 219.6; 9: 212; 15: 1.5; 18: 80; 19: 48.6; 20: 360; 23: 180; 24: 360; 25: 2.2X104; 28: 10.6; 29: 4.4; 31: 1.1; 52: 12; 55: 1720 |  |  |  | Non complying | Non complying |  | 7.7 | 102 | 288 |  | 212 | 1280 | 501.9 | 256.2 | 283.6 | [5 empty] | 4.2 |  |  | 156 | 82.6 | 104.2 |  |  | 210 | 600 | 5.4X104 |  |  | 16.1 | 5.8 |  | 2.1 | [20 empty] | 36 |  |  | 2358
| August, 1st Phase, 2026 | [9 empty] | 04.08.2026 | HRL/WW-I/2026/666-667 A dt. 18.08.2026 | - | 1: 7.4; 2: 16; 3: 120; 5: 42; 6: 882; 7: 394.3; 8: 219.6; 9: 154.7; 18: 344; 19: 34; 20: 116.2; 23: 180; 24: 430; 25: 120; 28: 39.7; 29: 0.6; 31: 0.8; 52: BDL(DL=4); 55: 1882 |  | 2.1 | 0.8 | Non complying | Non complying | Flow meter not working | 8.6 | 110 | 264 |  | 212 | 1424 | 618.9 | 610 | 485.6 | [8 empty] | 652 | 189.5 | 160.3 |  |  | 500 | 1180 | 4.2X104 |  |  | 49.3 | 17.6 |  | 5.2 | [20 empty] | 24 |  |  | 2456 |  | 4.3 | 4.2
2 | (BHI-STP-002) 10 MLD STP , Bhiwani by PHED Phase-II in 24.3.2014 (MBBR) |  | 20 | 6.5-8.0 | 100 | 40
[11 empty] | 14.01.2026 | 2038 dt. 29.01.2026 |  | 1: 7.53; 2: 102; 3: 416; 5: 245; 11: 14.01; 25: 3900 |  |  |  | Non complying | Non complying
[11 empty] | 05.02.2026 | 2267 dt. 13.02.2026 |  | 1: 6.71; 2: 82; 3: 370.9; 5: 175; 11: 15.6 |  |  |  | Non complying | Non complying
[11 empty] | 27.03.2026 | 2696 dt. 04.04.2026 |  | 1: 6.82; 2: 75; 3: 336; 5: 180; 11: 24.56; 25: 4100 |  |  |  | Non complying | Non complying
[11 empty] | 13.04.2026 | 119 dt. 23.04.2026 |  | 1: 7.15; 2: 96; 3: 370.9; 5: 220; 11: 28.14; 25: 5800 |  |  |  | Non complying | Non complying
[11 empty] | 14.05.2026 | HRL/WW-I/2026/131 dt. 20.05.2026 |  | 1: 8.8; 2: 64; 3: 128; 5: 156; 11: 34.2; 25: 100 |  |  |  | Non complying | Non complying
[11 empty] | 03.06.2026 | HRL/WW-I/2026/274-A dt. 08.06.2026 |  | 1: 8.7; 2: 72; 3: 144; 5: 148; 11: 36; 25: 4.8 X10 (3) |  |  |  | Non complying | Non complying
| July, 2026 | [9 empty] | Under maintenance during inspection
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | HRL/WW-I/2026/542--A dt. 30.07.2026 |  | 1: 8.5; 2: 80; 3: 128; 5: 96; 6: 96; 7: 441.7; 8: 292.8; 9: 274.2; 15: 2.1; 18: 172; 19: 136.1; 20: 960; 23: 240; 24: 960; 25: 4.8X103; 28: 14.1; 29: 8; 31: 1.8; 52: 14; 55: 3248 |  |  |  | Non complying | Non complying
| August, 1st Phase, 2026 | [9 empty] | 04.08.2026 | HRL/WW-I/2026/663 A dt. 18.08.2026 |  | 1: 8.2; 2: 72; 3: 160; 5: 82; 6: 552; 7: 848.5; 8: 85.4; 9: 374.5; 18: 496; 19: 34; 20: 76.2; 23: 70; 24: 330; 25: 1.5X104; 28: 66.8; 29: 0.4; 31: 4.8; 52: BDL(DL=4); 55: 1872 |  | 4.8 | 6.5 | Non complying | Non complying
3 | (BHI-STP-003) 15 MLD Phase-II, Bhiwani by PHED in 1.6.2014 |  | 20 | 6.5 to 8.00 | 100 | 40 | [92 empty] | 210000
[11 empty] | 14.01.2026 | 2042 dt. 29.01.2026 |  | 1: 7.14; 2: 8.6; 3: 48; 5: 19; 11: 6.68; 25: 79 |  |  |  | Complying | Complying |  | 7.85 | 108 | 432 |  | 185 | [5 empty] | 39.26 | [13 empty] | 4900
[11 empty] | 05.02.2026 | 2269 dt. 13.02.2026 |  | 1: 7.07; 2: 8.2; 3: 40.3; 5: 17; 11: 7.74; 25: 63 |  |  |  | Complying | Complying |  | 6.33 | 110 | 541.5 |  | 230 | [5 empty] | 44.18 | [13 empty] | 5800
[11 empty] | 27.03.2026 | 2695 dt. 07.04.2026 |  | 1: 7.21; 2: 9.2; 3: 44; 5: 19; 11: 10.25; 25: 79 |  |  |  | Complying | Complying |  | 6.94 | 102 | 424 |  | 275 | [5 empty] | 49.13 | [13 empty] | 8400
[11 empty] | 13.04.2026 | 122 dt. 23.04.2026 |  | 1: 6.79; 2: 6.8; 3: 36.2; 5: 13; 11: 6.64; 25: 58 |  |  |  | Complying | Complying |  | 6.91 | 120 | 475.7 |  | 325 | [5 empty] | 40.14 | [13 empty] | 9300
[11 empty] | 14.05.2026 | HRL/WW-I/2026/141-142-A dt. 20.05.2026 |  | 1: 7.1; 2: 22; 3: 144; 5: 96; 11: 12.4; 25: 210 |  |  |  | Non complying | Non complying |  | 7.2 | 102 | 524 |  | 249 | [5 empty] | 32.2 | [13 empty] | 7.2X10⁴
[11 empty] | 03.06.2026 | HRL/WW-I/2026/272-273-A dt. 08.06.2026 |  | 1: 7.8; 2: 18; 3: 80; 5: 16; 11: 10.4; 25: 150 |  |  |  | Non complying | Non complying |  | 8.8 | 162 | 472 |  | 218 | [5 empty] | 22.4 | [13 empty] | 6.4X10⁴
| July, 2026 1st Phase | [9 empty] | 07.07.2026 | HRL/WW-I/2026/433-434-A dt. 14.07.2026 |  | 1: 7.9; 2: 7.9; 3: 48; 5: 14; 11: 10; 25: 96; 52: BDL |  |  |  | Complying | Complying |  | 8.5 | 152 | 464 |  | 202 | [5 empty] | 28 | [13 empty] | 8.2X10⁴ | [26 empty] | 29
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | HRL/WW-I/2026/540-541-A dt. 30.07.2026 |  | 1: 7.8; 2: 8.1; 3: 32; 5: 14; 6: 212; 7: 180.7; 8: 103.7; 9: 143.2; 15: 0.6; 18: 46; 19: 24.3; 20: 180; 23: 85; 24: 180; 25: 80; 28: 8.6; 29: 2.1; 31: 0.6; 52: BDL(DL=4); 55: 962 |  |  |  | Complying | Complying |  | 8.1 | 110 | 188 |  | 170 | 1086 | 582 | 103.7 | 143.2 | [5 empty] | 2.4 |  |  | 140 | 140.9 | 152.3 |  |  | 245 | 960 | 5.2X104 |  |  | 12.7 | 9.2 |  | 2.1 | [20 empty] | 2.6 |  |  | 2160
| August, 1st Phase, 2026 | [9 empty] | 04.08.2026 | HRL/WW-I/2026/668-669 A dt. 18.08.2026 | Flow meter not working | 1: 7.5; 2: 6.8; 3: 32; 5: 12; 6: 656; 7: 409.3; 8: 97.6; 9: 244.5; 18: 345; 19: 34; 20: 100.2; 23: 80; 24: 390; 25: 56; 28: 42.1; 29: -0.6; 31: 0.9; 52: BDL(DL=4); 55: 1420 |  | 2.1 | 0.8 | Complying | Complying | Flow meter not working | 8.4 | 122 | 240 |  | 202 | 1752 | 718.8 | 634.4 | 456 | [8 empty] | 652 | 136.1 | 192.4 |  |  | 520 | 1040 | 3.6X104 |  |  | 50.9 | 12 |  | 4.2 | [20 empty] | 32 |  |  | 3260 |  | 5.6 | 4.8
4 | (BHI-STP-004) 15 MLD Phase-I, Bhiwani by PHED in 1.10.2013 |  | 20 | 6.5 to 8.00 | 100 | 40
[11 empty] | 14.01.2026 | 2043 dt. 29.01.2026 |  | 1: 7.52; 2: 7.2; 3: 40; 5: 16 |  |  |  | Complying | Complying |  | 7.29 | 105 | 424 |  | 215
[11 empty] | 05.02.2026 | 2268 dt. 13.02.2026 |  | 1: 7.13; 2: 7.8; 3: 36.2; 5: 15; 11: 9.6; 25: 58 |  |  |  | Complying | Complying |  | 7.26 | 96 | 387.07 |  | 270 | [5 empty] | 28.84 | [13 empty] | 4100
[11 empty] | 27.03.2026 | 2694 dt. 07.04.2026 |  | 1: 7.32; 2: 9.4; 3: 40; 5: 17; 11: 11.92; 25: 63 |  |  |  | Complying | Complying |  | 7.44 | 92 | 368 |  | 255 | [5 empty] | 37.54 | [13 empty] | 7000
[11 empty] | 13.04.2026 | 121 dt. 23.04.2026 |  | 1: 6.71; 2: 5.8; 3: 32.2; 5: 14; 11: 7.72; 25: 88 |  |  |  | Complying | Complying |  | 7.55 | 95 | 354.8 |  | 285 | [5 empty] | 31.94 | [13 empty] | 9300
[11 empty] | 14.05.2026 | HRL/WW-I/2026/129-130-A dt. 20.05.2026 |  | 1: 8.4; 2: 14; 3: 64; 5: 18; 11: 11.6; 25: 420 |  |  |  | Non complying | Non complying |  | 8.9 | 158 | 440 |  | 248 | [5 empty] | 28.4 | [13 empty] | 6.8X10⁴
[11 empty] | 03.06.2026 | HRL/WW-I/2026/266-267-A dt. 08.06.2026 |  | 1: 7.2; 2: 7.4; 3: 40; 5: 14; 11: 12.2; 25: 64 |  |  |  | Complying | Complying |  | 7.3 | 246 | 504 |  | 264 | [5 empty] | 30.4 | [13 empty] | 7.2X10⁴
| July, 2026 1st Phase | [9 empty] | 07.07.2026 | HRL/WW-I/2026/431-432-A dt. 14.07.2026 |  | 1: 7.6; 2: 8.6; 3: 40; 5: 8; 11: 12; 25: 72; 52: BDL |  |  |  | Complying | Complying |  | 8.4 | 148 | 408 |  | 196 | [5 empty] | 24 | [13 empty] | 6.4 X10⁴ | [26 empty] | 26
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | HRL/WW-I/2026/536-537-A dt. 30.07.2026 |  | 1: 7.5; 2: 8.2; 3: 36; 5: 18; 6: 290; 7: 150.5; 9: 188; 15: 0.8; 19: 24.3; 20: 180; 23: 100; 24: 180; 52: BDL(DL=4); 55: 980 |  |  |  | Complying | Complying |  | 8.1 | 96 | 196 |  | 156 | 1150 | 481.8 |  | 251.8 | [5 empty] | 2.8 |  |  |  | 72.6 | 144.2 |  |  | 280 | 660 | [27 empty] | 24 |  |  | 2240
| August, 1st Phase, 2026 | [9 empty] | 04.08.2026 | HRL/WW-I/2026/670-671 A dt. 18.08.2026 | Flow meter not working | 1: 7.3; 2: 8.2; 3: 44; 5: 8; 6: 432; 7: 618.9; 8: 146.4; 9: 368.1; 18: 459; 19: 51; 20: 124.3; 23: 120; 24: 520; 25: 72; 28: 49; 29: 0.4; 31: 0.8; 52: BDL(DL=4); 55: 1260 |  | 2.1 | 0.8 | Complying | Complying | Flow meter not working | 8.6 | 130 | 224 |  | 168 | 1560 | 648.9 | 658.8 | 482.6 | [8 empty] | 684 | 165.2 | 192.4 |  |  | 540 | 1160 | 5.6X104 |  |  | 51.1 | 14.8 |  | 3.6 | [20 empty] | 36 |  |  | 3880 |  | 4.2 | 4.5
5 | (BHI-STP-005) 10 MLD Bhiwani by HUDA in 1.1.2015 (SBR)
[11 empty] | 14.01.2026 | 2040 dt. 29.01.2026 |  | 1: 7.35; 2: 6.8; 3: 36; 5: 15; 11: 7.12; 25: 93 |  |  |  | Complying | Complying |  | 7.84 | 98 | 392 |  | 228 | [5 empty] | 30.82 | [13 empty] | 5000
[11 empty] | 05.02.2026 | 2266 dt. 13.02.2026 |  | 1: 6.75; 2: 9.2; 3: 48.3; 5: 18; 11: 6.62; 25: 58 |  |  |  | Complying | Complying |  | 8.1 | 94 | 370.9 |  | 250 | [5 empty] | 36.84 | [13 empty] | 4900
[11 empty] | 05.03.2026 | 2532 dt. 16.03.2026 |  | 1: 6.65; 2: 8.2; 3: 48; 5: 15; 11: 9.76; 25: 80 |  |  |  | Complying | Complying |  | 7.85 | 94 | 384 |  | 265 | [5 empty] | 39.72 | [13 empty] | 5800
[11 empty] | 13.04.2026 | 120 dt. 23.04.2026 |  | 1: 7.54; 2: 8.8; 3: 48.3; 5: 16; 11: 8.4; 25: 70 |  |  |  | Complying | Complying |  | 7.45 | 110 | 411.2 |  | 305 | [5 empty] | 41.08 | [13 empty] | 8400
[11 empty] | 14.05.2026 | HRL/WW-I/2026/133-134-A dt. 20.05.2026 |  | 1: 7.8; 2: 8.8; 3: 42; 5: 18; 11: 12.2; 25: 72 |  |  |  | Complying | Complying |  | 8.9 | 124 | 396 |  | 272 | [5 empty] | 26.4 | [13 empty] | 8.6X10⁴
[11 empty] | 03.06.2026 | HRL/WW-I/2026/268-269-A dt. 08.06.2026 |  | 1: 7.6; 2: 8.7; 3: 44; 5: 17; 11: 8.2; 25: 82 |  |  |  | Complying | Complying |  | 8.8 | 132 | 504 |  | 258 | [5 empty] | 32.4 | [13 empty] | 3.2X10⁴
| July, 2026 1st Phase | [9 empty] | 07.07.2026 | HRL/WW-I/2026/435-436-A dt. 14.07.2026 |  | 1: 7.9; 2: 62; 3: 144; 5: 38; 11: 18; 25: 3.2X102; 52: BDL |  |  |  | Non complying | Non complying |  | 8.6 | 124 | 456 |  | 224 | [5 empty] | 30 | [13 empty] | 3.6X10⁴ | [26 empty] | 30
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | HRL/WW-I/2026/538-539-A dt. 30.07.2026 |  | 1: 7.9; 2: 7.5; 3: 48; 5: 12; 6: 242; 7: 170.6; 8: 109.8; 9: 152.1; 15: 0.9; 18: 36; 19: 24.3; 20: 180; 23: 90; 24: 180; 25: 72; 28: 6.7; 29: 2.2; 31: 0.8; 52: BDL(DL=4); 55: 2180 |  |  |  | Complying | Complying |  | 7 | 105 | 180 |  | 176 | 920 | 522 | 292.8 | 248.9 | [5 empty] | 1.8 |  |  | 156 | 145.8 | 152.3 |  |  | 240 | 980 | 6.8X104 |  |  | 12.7 | 9.2 |  | 1.8 | [20 empty] | 28 |  |  | 2180
| August, 1st Phase, 2026 | [9 empty] | 04.08.2026 | HRL/WW-I/2026/664-665 A dt. 18.08.2026 | Flow meter not working | 1: 7.5; 2: 7.2; 3: 40; 5: 9; 6: 484; 7: 449.2; 8: 85.4; 9: 185.6; 18: 320; 19: 250.3; 20: 164.3; 23: 70; 24: 1440; 25: 32; 28: 22.2; 29: 13.8; 31: 1.3; 52: BDL(DL=4); 55: 1270 |  | 2.1 | 0.8 | Complying | Complying | Flow meter not working | 8.6 | 122 | 316 |  | 146 | 1278 | 579 | 683.4 | 528.1 | [8 empty] | 425 | 204.1 | 320.6 |  |  | 560 | 1640 | 4.8X104 |  |  | 26.2 | 12 |  | 3.9 | [20 empty] | 32 |  |  | 3672 |  | 39 | 5.2
Charkhi Dadri
6 | (BHI-STP-006) 5 MLD STP Jhajjar/ Delhi Road, Charkhi Dadri Bhiwani by PHED in 1.8.2014
[11 empty] | 20.01.2026 | 2109 dt. 03.02.2026 |  | 1: 7.51; 2: 78; 3: 320; 5: 210; 11: 24.26; 25: 4900 |  |  |  | Non-Complying | Non-Complying |  | 7.82 | 105 | 424 |  | 245 | [5 empty] | 31.04 | [13 empty] | 9300
[11 empty] | 27.02.2026 | 2498 dt. 11.03.2026 |  | 1: 7.84; 2: 82; 3: 336; 5: 240; 11: 22.02; 25: 5800 |  |  |  | Non-Complying | Non-Complying |  | 8.12 | 115 | 464 |  | 270 | [5 empty] | 45.49 | [13 empty] | 8400
[11 empty] | 23.03.2026 | 2654 dt. 01.04.2026 |  | 1: 7.29; 2: 92; 3: 376; 5: 215; 11: 15.81; 25: 6300 |  |  |  | Non-Complying | Non-Complying |  | 7.93 | 124 | 496 |  | 258 | [5 empty] | 39.84 | [13 empty] | 7900
Apr.,2026
[11 empty] | 15.05.2026 | HRL/WW-I/2026/147-148 A dt. 20.05.2026 |  | 1: 6.6; 2: 18; 3: 192; 5: 17; 11: 18.6; 25: 9.6X10 (3) |  |  |  | Non-Complying | Non-Complying |  | 7.2 | 112 | 448 |  | 256 | [5 empty] | 36.2 | [13 empty] | 8.6 X 10⁴
[11 empty] | 16.06.2026 | HRL/WW-I/2026/334-335 A dt. 18.06.2026 |  | 1: 7.4; 2: 22; 3: 272; 5: 48; 11: 16.4; 25: 8.6X10³ |  |  |  | Non-Complying | Non-Complying |  | 8.2 | 106 | 424 |  | 224 | [5 empty] | 32.4 | [13 empty] | 7.2 X 10⁴
[11 empty] | 03.07.2026 | HRL/WW-I/ 2026/406-407-A Dated 09.07.2026 |  | 1: 7.5; 2: 34; 3: 180; 5: 45; 11: 28; 25: 4.2×10³; 52: BDL |  |  |  | Non-Complying | Non-Complying |  | 288 | 96 | 7.4 |  | 172 | [5 empty] | 36 | [13 empty] | 2.1×10⁴ | [26 empty] | 48
7 | (BHI-STP-007) 5 MLD STP Chiriya Road, Charkhi Dadri, Bhiwani by PHED 20.7.2013 |  | 30 | 6.5 to 8.00 | 100 | 40
[11 empty] | 20.01.2026 | 2110 dt. 03.02.2026 |  | 1: 7.12; 2: 80; 3: 328; 5: 195; 11: 14.01; 25: 6300 |  |  |  | Non-Complying | Non-Complying |  | 4.83 | 110 | 488 |  | 270 | [5 empty] | 40.84 | [13 empty] | 7000
[11 empty] | 27.02.2026 | 2499 dt. 11.03.2026 |  | 1: 7.26; 2: 72; 3: 304; 5: 145; 25: 7000 |  |  |  | Non-Complying | Non-Complying |  | 6.75 | 98 | 392 |  | 250 | [5 empty] | 36.82 | [13 empty] | 8400
[11 empty] | 23.03.2026 | 2653 dt. 01.04.2026 |  | 1: 7.13; 2: 88; 3: 352; 5: 172; 11: 16.64; 25: 7000 |  |  |  | Non-Complying | Non-Complying |  | 6.43 | 108 | 432 |  | 285 | [5 empty] | 43.12 | [13 empty] | 9300
Apr.,2026
[11 empty] | 15.05.2026 | HRL/WW-I/2026/145-146 A dt. 20.05.2026 |  | 1: 7.9; 2: 122; 3: 304; 5: 348; 11: 18.6; 25: 860 |  |  |  | Non-Complying | Non-Complying |  | 8.4 | 138 | 472 |  | 396 | [5 empty] | 38.2 | [13 empty] | 6.8 X10⁴
[11 empty] | 16.06.2026 | HRL/WW-I/2026/332-333 A dt. 18.06.2026 |  | 1: 7.8; 2: 118; 3: 376; 5: 312; 11: 16.4; 25: 820 |  |  |  | Non-Complying | Non-Complying |  | 8.5 | 132 | 440 |  | 372 | [5 empty] | 40.2 | [13 empty] | 6.2 X10⁴
[11 empty] | 03.07.2026 | HRL/WW-I/ 2026/404-405A Dated 09.07.2026 |  | 1: 7.2; 2: 88; 3: 204; 5: 140; 11: 12; 25: 560; 52: BDL |  |  |  | Non-Complying | Non-Complying |  | 304 | 102 | 6.9 |  | 264 | [5 empty] | 28 | [13 empty] | 3.2×10⁴ | [26 empty] | 32
8 | (BHI-STP-008) 4.5 MLD STP Bawani Khera by PHED in 31.12.2015 |  | 30 | 6.5 to 8.00 | 100 | 40
[11 empty] | 14.01.2026 | 2045 dt. 29.01.2026 |  | 1: 7.42; 2: 8.2; 3: 48; 5: 19; 11: 5.6; 25: 84 |  |  |  | Complying | Complying |  | 7.56 | 85 | 376 |  | 245 | [5 empty] | 43.12 | [13 empty] | 9300
[11 empty] | 16.02.2026 | 2350 dt. 23.02.2026 |  | 1: 7.48; 2: 7.8; 3: 40; 5: 18; 11: 6.92; 25: 63 |  |  |  | Complying | Complying |  | 7.41 | 96 | 392 |  | 265 | [5 empty] | 46.84 | [13 empty] | 7900
[11 empty] | 05.03.2026 | 2530 dt. 16.03.2026 | 33759.784 | 1: 7.49; 2: 6.4; 3: 36; 5: 17; 11: 8.28; 25: 79 |  |  |  | Complying | Complying | - | 7.58 | 92 | 368 |  | 235 | [5 empty] | 42.14 | [13 empty] | 8400
[11 empty] | 13.04.2026 | 126 dt. 28.04.2026 |  | 1: 7.19; 2: 5.8; 3: 32; 5: 13; 11: 7; 25: 63 |  |  |  | Complying | Complying |  | 7.64 | 90 | 336 |  | 245 | [5 empty] | 49.14 | [13 empty] | 9300
[11 empty] | 14.05.2026 | HRL/WW-I/2026/135-136-A dt. 20.05.2026 |  | 1: 7.4; 2: 7.2; 3: 36; 5: 12; 11: 14.6; 25: 72 |  |  |  | Complying | Complying |  | 7.3 | 296 | 516 |  | 286 | [5 empty] | 28 | [13 empty] | 6.8X10⁴
[11 empty] | 03.06.2026 | HRL/WW-I/2026/264-265-A dt. 08.06.2026 |  | 1: 7.4; 2: 7.8; 3: 40; 5: 14; 11: 12.2; 25: 64 |  |  |  | Complying | Complying |  | 7.1 | 302 | 400 |  | 242 | [5 empty] | 32 | [13 empty] | 7.2X10⁴
| July, 2026 1st Phase | [9 empty] | 07.07.2026 | HRL/WW-I/2026/427-428-A dt. 14.07.2026 |  | 1: 8.1; 2: 45; 3: 160; 5: 45; 11: 28; 25: 7.2X103; 52: BDL |  |  |  | Non-Complying | Non-Complying |  | 8.8 | 145 | 488 |  | 296 | [5 empty] | 28 | [13 empty] | 4.8X10⁴ | [26 empty] | 28
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | HRL/WW-I/2026/532-533-A dt. 30.07.2026 |  | 1: 7.9; 2: 38; 3: 128; 5: 36; 6: 956; 7: 221.8; 8: 146.4; 9: 225.1; 15: 1.7; 18: 109; 19: 63.2; 20: 500; 23: 120; 24: 500; 25: 360; 28: 12.2; 29: 2.8; 31: 1.8; 52: BDL(DL=4); 55: 2816 |  |  |  | Non complying | Non complying |  | 8.1 | 112 | 248 |  | 148 | 1456 | 341.3 | 341.6 | 281.4 | [5 empty] | 2.1 |  |  | 176 | 150.7 | 208.4 |  |  | 280 | 1140 | 8.6X104 |  |  | 13.1 | 7.6 |  | 3.2 | [20 empty] | 28 |  |  | 3541
| August, 1st Phase, 2026 | [9 empty] | 04.08.2026 | HRL/WW-I/2026/672-673 A dt. 18.08.2026 | Flow meter not working | 1: 7.1; 2: 7.8; 3: 40; 5: 9; 6: 480; 7: 329.4; 8: 73.2; 9: 183.4; 18: 243; 19: 94.8; 20: 140.3; 23: 60; 24: 740; 25: 80; 28: 22.4; 29: 2; 31: 0.9; 52: BDL(DL=4); 55: 1413 |  | 1.6 | 0.4 | Complying | Complying | Flow meter not working | 8.8 | 116 | 216 |  | 178 | 1654 | 678.8 | 780.8 | 252.4 | [8 empty] | 524 | 179.8 | 216.4 |  |  | 640 | 1280 | 4.8X104 |  |  | 37.2 | 16.8 |  | 4 | [20 empty] | 28 |  |  | 3620 |  | 4.5 | 6.1
9 | (BHI-STP-009) 3.5 MLD STP Loharu Bhiwani by PHED in 30.11.2015 |  | 30 | 6.5 to 8.00 | 100 | 40
[11 empty] | 14.01.2026 | 2037 dt. 29.01.2026 |  | 1: 7.21; 2: 8.2; 3: 44; 5: 15; 11: 7.6; 25: 79 |  |  |  | Complying | Complying |  | 7.69 | 88 | 360 |  | 220 | [5 empty] | 34.28 | [13 empty] | 8400
[11 empty] | 25.11.2025 | 1644 dt. 08.12.2025 |  | 1: 7.73; 2: 17; 3: 80; 5: 29; 11: 18.21; 25: 490 |  |  |  | Non-Complying | Non-Complying |  | 8.12 | 102 | 416 |  | 205 | [5 empty] | 32.15 | [13 empty] | 8400
[11 empty] | 16.02.2026 | 2349 dt. 24.02.2026 |  | 1: 7.84; 2: 8.2; 3: 44; 5: 17; 11: 5.44; 25: 58 |  |  |  | Complying | Complying |  | 7.61 | 80 | 368 |  | 245 | [5 empty] | 31.54 | [13 empty] | 8400
[11 empty] | 05.03.2026 | 2529 dt. 16.03.2026 | 1.1 | 1: 7.65; 2: 8.8; 3: 48; 5: 15; 11: 6.78; 25: 93 |  |  |  | Complying | Complying | - | 7.19 | 95 | 384 |  | 250 | [5 empty] | 34.52 | [13 empty] | 7000
[11 empty] | 13.04.2026 | 124 dt. 23.04.2026 |  | 1: 7.27; 2: 7.2; 3: 48.3; 5: 18; 11: 5.6; 25: 49 |  |  |  | Complying | Complying |  | 7.21 | 80 | 322.5 |  | 265 | [5 empty] | 32.94 | [13 empty] | 9300
[11 empty] | 13.05.2026 | HRL/WW-I/2026/111-112-A dt. 20.05.2026 |  | 1: 8; 2: 7.8; 3: 32; 5: 15; 25: 82 |  |  |  | Complying | Complying |  | 8.7 | 98 | 248 |  | 212 | [19 empty] | 5.6X10⁴
[11 empty] | 09.06.2026 | HRL/WW-I/2026/307-308-A dt. 16.06.2026 |  | 1: 7.9; 2: 7.6; 3: 34; 5: 14; 11: 9.8; 25: 56 |  |  |  | Complying | Complying |  | 8.8 | 96 | 232 |  | 202 | [5 empty] | 36.4 | [13 empty] | 4.2X10⁴
| July, 2026 1st Phase | [9 empty] | 07.07.2026 | HRL/WW-I/2026/423-424-A dt. 14.07.2026 |  | 1: 7.8; 2: 36; 3: 88; 5: 25; 11: 10; 25: 720; 52: BDL |  |  |  | Non-Complying | Non-Complying |  | 8.6 | 102 | 248 |  | 218 | [5 empty] | 32 | [13 empty] | 4.5X10⁴ | [26 empty] | 21
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | HRL/WW-I/2026/544--A dt. 30.07.2026 |  | 1: 8.2; 2: 72; 3: 136; 5: 80; 6: 1894; 7: 481.8; 8: 256.4; 9: 294.8; 18: 158; 19: 82.6; 20: 600; 23: 210; 24: 600; 25: 7.2X104; 28: 16.3; 29: 5.8; 31: 1.9; 52: 15; 55: 3414 |  | 2.1 |  | Non complying | Non complying
| August, 1st Phase, 2026 | [9 empty] | 06.08.2026 | HRL/WW-I/2026/692-693 A dt. 18.08.2026 | Flow meter not working | 1: 5.2; 2: 64; 3: 120; 5: 86; 6: 1270; 7: 494.2; 8: 146.2; 9: 198.4; 18: 580; 19: 19.4; 20: 76.2; 23: 120; 24: 270; 25: 6.4X103; 28: 83.9; 29: 0.2; 31: 0.9; 52: 8; 55: 4840 |  | 1.6 | 0.4 | Non complying | Non complying | Flow meter not working | 8.7 | 186 | 408 |  | 146 | 2460 | 519.4 | 683.2 | 524.6 | [8 empty] | 636 | 38.9 | 112.2 |  |  | 560 | 440 | 4.8X104 |  |  | 73.2 | 8.8 |  | 5.6 | [20 empty] | 28 |  |  | 5656 |  | 3.5 | 4.3
10 | (BHI-STP-010) 3 MLD STP Tosham, Bhiwani by PHED on 01.07.2014 |  | 10 | 6.5 to 8.00 | 50 | 20
[11 empty] | 14.01.2026 | 2036 dt. 29.01.2026 |  | 1: 7.19; 2: 7.2; 3: 44; 5: 19; 11: 7; 25: 84 |  |  |  | Complying | Complying |  | 7.84 | 118 | 472 |  | 225 | [5 empty] | 34.82 | [13 empty] | 7900
[11 empty] | 16.02.2026 | 2347 dt. 24.02.2026 |  | 1: 7.2; 2: 8.4; 3: 48; 5: 17; 25: 63 |  |  |  | Complying | Complying |  | 7.72 | 85 | 344 |  | 230 | [19 empty] | 7900
[11 empty] | 05.03.2026 | 2531 dt. 16.03.2026 | 912810045 | 1: 7.43; 2: 45; 3: 208; 5: 42; 25: 790 |  |  |  | Non Complying | Non Complying | 703624.066 | 7.94 | 90 | 376 |  | 210 | [19 empty] | 9300
[11 empty] | 13.04.2026 | 123 dt. 23.04.2026 | 912810045 | 1: 7.31; 2: 16; 3: 72.5; 5: 31; 25: 210 |  |  |  | Non Complying | Non Complying | 703624.066 | 8.02 | 82 | 358.8 |  | 275 | [19 empty] | 8400
[11 empty] | 14.05.2026 | HRL/WW-I/2026/139-140-A dt. 20.05.2026 | 2.5 | 1: 7.3; 2: 9.2; 3: 56; 5: 17; 11: 21.6; 25: 86 |  |  |  | Non Complying | Non Complying | 2.6 | 7.4 | 118 | 496 |  | 296 | [5 empty] | 34.6 | [13 empty] | 6.8X10⁴
[11 empty] | 11.06.2026 | HRL/WW-I/2026/321-322-A dt. 16.06.2026 |  | 1: 8.1; 2: 36; 3: 68; 5: 18; 11: 16; 25: 860 |  |  |  | Non Complying | Non Complying |  | 8.8 | 116 | 368 |  | 268 | [5 empty] | 36.8 | [13 empty] | 6.5X10⁴
| July, 2026 1st Phase | [9 empty] | 07.07.2026 | HRL/WW-I/2026/437-438-A dt. 14.07.2026 |  | 1: 8.2; 2: 32; 3: 64; 5: 22; 11: 18; 25: 520; 52: BDL |  |  |  | Non Complying | Non Complying |  | 8.6 | 104 | 352 |  | 272 | [5 empty] | 32 | [13 empty] | 4.8 X10⁴ | [26 empty] | 26
| July, 2026 2nd Phase | [9 empty] | 19.07.2026 | HRL/WW-I/2026/517-518-A dt. 30.07.2026 |  | 1: 7.8; 2: 24; 3: 58; 5: 56; 6: 1140; 7: 401.5; 8: 134.2; 9: 380.3; 15: 1.8; 18: 118; 19: 131.2; 20: 960; 23: 110; 24: 960; 25: 4.8X104; 28: 9.6; 29: 4.6; 31: 2.1; 52: 7; 55: 3318 |  |  |  | Non complying | Non complying |  | 7.7 | 126 | 368 |  | 236 | 1628 | 572.2 | 268.4 | 443.6 | [5 empty] | 3.8 |  |  | 256 | 145.8 | 216.4 |  |  | 220 | 1140 | 4.8X104 |  |  | 9.6 | 4.6 |  | 2.1 | [20 empty] | 28 |  |  | 3624
11 | (BHI-STP-011) 4 MLD STP Siwani Bhiwani by PHED in 9.9.2014 |  | 30 | 6.5 to 8.00 | 100 | 40
[11 empty] | 14.01.2026 | 2035 dt. 29.01.2026 |  | 1: 7.72; 2: 6.2; 3: 32; 5: 13; 11: 8.4; 25: 93 |  |  |  | Complying | Complying |  | 8.13 | 95 | 424 |  | 270 | [5 empty] | 39.28 | [13 empty] | 13000
[11 empty] | 16.02.2026 | 2348 dt. 24.02.2026 |  | 1: 7.38; 2: 6.8; 3: 40; 5: 15; 11: 7.48; 25: 79 |  |  |  | Complying | Complying |  | 7.47 | 86 | 384 |  | 215 | [5 empty] | 38.32 | [13 empty] | 11000
[11 empty] | 05.03.2026 | 2528 dt. 16.03.2026 |  | 1: 7.79; 2: 7.6; 3: 40; 5: 14; 11: 7.92; 25: 63 |  |  |  | Complying | Complying |  | 7.46 | 95 | 392 |  | 245 | [5 empty] | 46.72 | [13 empty] | 4900
[11 empty] | 13.04.2026 | 125 dt. 23.04.2026 |  | 1: 6.99; 2: 8.2; 3: 44.3; 5: 17; 11: 12.72; 25: 93 |  |  |  | Complying | Complying |  | 7.92 | 120 | 491.9 |  | 380 | [5 empty] | 38.24 | [13 empty] | 7000
[11 empty] | 14.05.2026 | HRL/WW-I/2026/137-138-A dt. 20.05.2026 | 2.5 | 1: 7.4; 2: 9.2; 3: 68; 5: 18; 11: 22; 25: 90 |  |  |  | Non Complying | Non Complying | - | 7.2 | 148 | 448 |  | 234 | [5 empty] | 36.2 | [13 empty] | 5.2X10⁴
[11 empty] | 10.06.2026 | HRL/WW-I/2026/305-306-A dt. 16.06.2026 |  | 1: 7.3; 2: 8.2; 3: 44; 5: 16; 11: 8.4; 25: 86 |  |  |  | Complying | Complying |  | 7.8 | 120 | 416 |  | 218 | [5 empty] | 34.4 | [13 empty] | 4.8X10⁴
| July, 2026 1st Phase | [9 empty] | 07.07.2026 | HRL/WW-I/2026/425-426-A dt. 14.07.2026 |  | 1: 7.2; 2: 7.5; 3: 16; 5: 14; 11: 6; 25: 32; 52: BDL |  |  |  | Complying | Complying |  | 8.2 | 112 | 384 |  | 202 | [5 empty] | 30 | [13 empty] | 3.6X10⁴ | [26 empty] | 30
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | HRL/WW-I/2026/543-A dt. 30.07.2026 |  | 1: 8.6; 2: 172; 3: 304; 5: 148; 6: 1960; 7: 391.5; 8: 268.4; 9: 321.8; 15: 2.6; 18: 162; 19: 97.2; 20: 700; 23: 220; 24: 700; 25: 5.2X104; 28: 15.5; 29: 6.4; 31: 1.4; 52: 32; 55: 3652 |  |  |  | Non complying | Non complying
| August, 1st Phase, 2026 | [9 empty] | 06.08.2026 | HRL/WW-I/2026/694-695 A dt. 18.08.2026 |  | 1: 5.8; 2: 36; 3: 136; 5: 36; 6: 1870; 7: 434.3; 8: 73.2; 9: 524.6; 15: 1.1; 18: 238.5; 19: 58.3; 20: 44.1; 23: 60; 24: 350; 25: 3.6X103; 28: 33.3; 29: 3.8; 31: 1.2; 52: 16; 55: 3612 |  |  | 0.4 | Non complying | Non complying |  | 8.6 | 146 | 276 |  | 148 | 2170 | 479.2 | 463.2 | 772.5 | [5 empty] | 2.1 |  |  | 274 | 87.5 | 56.1 |  |  | 380 | 500 | 4.2X104 |  |  | 32.3 | 12 |  | 7.2 | [20 empty] | 32 |  |  | 3956 |  |  | 0.4
Mohindergarh
12 | (MHD-STP-001) 6.5 MLD STP, Dulana Road, Mohindergarh by PHED in 1.9.2014 |  | 20 | 7-8.00 | 100 | 40
[11 empty] | 14.01.2026 | 2024 dt. 28.01.2026 |  | 1: 7.23; 2: 9.8; 3: 47.8; 5: 19; 11: 7; 25: 93 |  |  |  | Complying | Complying |  | 7.84 | 115 | 462.1 |  | 260 | [5 empty] | 40.16 | [13 empty] | 7900
[11 empty] | 03.02.2026 | 2224 dt. 11.02.2026 | - | 1: 7.07; 2: 8; 3: 40.3; 5: 15; 11: 9.18; 25: 70 |  |  |  | Complying | Complying | - | 7.71 | 110 | 451.5 |  | 270 | [19 empty] | 38.16
[11 empty] | 24.03.2026 | 2269 dt. 04.04.2026 | - | 1: 6.94; 2: 22; 3: 84; 5: 37; 11: -; 25: 160 |  |  |  | Non Complying | Non Complying | - | 7.84 | 98 | 408 |  | 285 | [5 empty] | - | [13 empty] | 7000
[11 empty] | 20.04.2026 | 167 dt. 29.04.2026 | - | 1: 7.76; 2: 13; 3: 68; 5: 24; 11: -; 25: 196 |  |  |  | Non Complying | Non Complying | - | 7.91 | 92 | 384 |  | 305 | [5 empty] | - | [13 empty] | 9300
[11 empty] | 11.05.2026 | 144-145 dt. 21.05.2026 | - | 1: 7.9; 2: 6; 3: 17; 5: 10; 11: BDL; 25: 44 |  |  |  | Complying | Complying | - | 6.5 | 115 | 258 |  | 148 | [5 empty] | 14 | [13 empty] | 188000
[11 empty] | 03.06.2026 | 544-545 dt. 11.06.2026 | - | 1: 7.5; 2: 7; 3: 36; 5: 12; 11: BDL; 25: 62 |  |  |  | Complying | Complying | - | 6.4 | 95 | 324 |  | 248 | [5 empty] | 26 | [13 empty] | 190000
[11 empty] | 06.07.2026 | 825-826 dt. 15.07.2026 |  | 1: 7.3; 2: 32; 3: 108; 5: 54; 11: 4.2; 14: 0.6; 25: 652; 52: 4; 55: 1220 |  |  |  | Non Complying | Non Complying |  | 6.8 | 115 | 352 |  | 306 | [5 empty] | 38 |  |  | 3.1 | [10 empty] | 89000 | [26 empty] | 18 |  |  | 1240
13 | (MHD-STP-002) 2 MLD STP, Ateli Mandi, Mohindergarh by PHED in 30.6.2016 |  | 20 | 7-8.5 | 100 | 40
[11 empty] | 14.01.2026 | 2030 dt. 28.01.2026 | 99.1 | 1: 7.24; 2: 7.4; 3: 43.8; 5: 15; 11: 5.6; 25: 58 |  |  |  | Complying | Complying | - | 7.48 | 90 | 358.5 |  | 205 | [5 empty] | 33.83 | [13 empty] | 7900
[11 empty] | 03.02.2026 | 2222 dt. 11.02.2026 | 96.7 | 1: 7.11; 2: 18; 3: 72.5; 5: 30; 11: 7; 25: 210 |  |  |  | Non Complying | Non Complying | 98.5 | 7.72 | 95 | 395.1 |  | 235 | [5 empty] | 39.16 | [13 empty] | 8400
[11 empty] | 24.03.2026 | 2671 dt. 06.04.2026 |  | 1: 6.89; 2: 9; 3: 44; 5: 17; 11: 8.24; 25: 70 |  |  |  | Complying | Complying |  | 7.88 | 102 | 416 |  | 270 | [5 empty] | 40.29 | [13 empty] | 9300
[11 empty] | 20.04.2026 | 169 dt. 29.04.2026 |  | 1: 6.92; 2: 9.4; 3: 48; 5: 18; 11: -; 25: 84 |  |  |  | Complying | Complying | - | 7.25 | 110 | 456 |  | 295 | [5 empty] | - | [13 empty] | 11000
[11 empty] | 12.05.2026 | 136-37 dt. 21.05.2026 | - | 1: 6.9; 2: 5; 3: 26; 5: 14; 11: ND; 25: 64 |  |  |  | Complying | Complying | - | 6.6 | 135 | 284 |  | 152 | [5 empty] | 16 | [13 empty] | 148000
[11 empty] | 03.06.2026 | 546-547 dt. 11.06.2026 | - | 1: 7.2; 2: 8; 3: 44; 5: 17; 11: BDL; 25: 76 |  |  |  | Complying | Complying | - | 6.9 | 105 | 332 |  | 186 | [5 empty] | 19 | [13 empty] | 120000
[11 empty] | 06.07.2026 | 831-832 dt. 15.07.2026 |  | 1: 7.2; 2: 9; 3: 44; 5: 17; 11: 4.6; 14: ND; 25: 84; 52: 19; 55: 1460 |  |  |  | Complying | Complying |  | 6.8 | 115 | 372 |  | 320 | [5 empty] | 32 |  |  | 2.6 | [10 empty] | 72000 | [26 empty] | 19 |  |  | 1750
14 | (MHD-STP-003) 3 MLD STP Kanina, Mohindergarh by PHED in 30.4.2016 |  | 20 | 7.0-8.5 | 100 | 40
[11 empty] | 14.01.2026 | 2025 dt. 28.01.2026 | 262967.51 | 1: 7.27; 2: 8.8; 3: 39.8; 5: 17; 11: 7; 25: 63 |  |  |  | Complying | Complying | 104.4 | 7.43 | 125 | 501.9 |  | 220 | [5 empty] | 28.02 | [13 empty] | 7900
[11 empty] | 03.02.2026 | 2225 dt. 11.02.2026 | 107.7 | 1: 7.78; 2: 9.2; 3: 44.3; 5: 18; 11: 6.68; 25: 84 |  |  |  | Complying | Complying | - | 7.21 | 90 | 370.9 |  | 250 | [5 empty] | 30.82 | [13 empty] | 6300
[11 empty] | 24.03.2026 | 2668 dt. 06.04.2026 | 89.9 | 1: 7.2; 2: 8.5; 3: 48; 5: 18; 11: -; 25: 79 |  |  |  | Complying | Complying | 83 | 7.44 | 88 | 344 |  | 230 | [5 empty] | - | [13 empty] | 8400
[11 empty] | 20.04.2026 | 170 dt. 29.04.2026 | - | 1: 7.15; 2: 7.6; 3: 44; 5: 18; 11: 8.4; 25: 93 |  |  |  | Complying | Complying | - | 8.12 | 104 | 392 |  | 275 | [5 empty] | 33.14 | [13 empty] | 7000
[11 empty] | 12.05.2026 | 134-135 dt. 21.05.2026 | - | 1: 7.1; 2: 9; 3: 36; 5: 8; 11: 5; 25: 84 |  |  |  | Complying | Complying | - | 6.8 | 135 | 284 |  | 286 | [5 empty] | 13 | [13 empty] | 154000
[11 empty] | 02.06.2026 | 542-543 dt. 21.05.2026 | - | 1: 7.3; 2: 5; 3: 32; 5: 12; 11: BDL; 25: 76 |  |  |  | Complying | Complying | - | 6.9 | 120 | 344 |  | 282 | [5 empty] | 17 | [13 empty] | 110000
[11 empty] | 06.07.2026 | 827-828 dt. 15.07.2026 |  | 1: 7.3; 2: 9; 3: 48; 5: 18; 11: 6; 14: 0.7; 25: 94; 52: BDL; 55: 1670 |  |  |  | Complying | Complying |  | 6.9 | 105 | 352 |  | 284 | [5 empty] | 34 |  |  | 2.9 | [10 empty] | 84000 | [26 empty] | 18 |  |  | 1840
15 | (MHD-STP-004) 7.5 MLD Rewari Road, Narnaul, Mohindergarh by PHED in 29.4.2015 |  | 20 | 7-8.5 | 100 | 40
[11 empty] | 14.01.2026 | 2027 dt. 28.01.2026 | 7.5 | 1: 7.32; 2: 15; 3: 71.7; 5: 28; 11: 12.6; 25: 580 |  |  |  | Non Complying | Non Complying | - | 7.84 | 105 | 422.3 |  | 255 | [5 empty] | 30.82 | [13 empty] | 11000
[11 empty] | 04.02.2026 | 2226 dt. 11.02.2026 | 312 | 1: 6.99; 2: 16; 3: 68.5; 5: 28; 11: 8.2; 25: 210 |  |  |  | Non Complying | Non Complying | 7.5 | 7.68 | 120 | 467.7 |  | 230 | [5 empty] | 42.26 | [13 empty] | 9300
[11 empty] | 09.03.2026 | 2567 dt. 17.03.2026 | 7.5 | 1: 7.23; 2: 19; 3: 108; 5: 42; 11: 7.72; 25: 580 |  |  |  | Non Complying | Non Complying | 7.5 | 8.13 | 110 | 448 |  | 295 | [5 empty] | 34.18 | [13 empty] | 11000
[11 empty] | 20.04.2026 | 164 dt. 29.04.2026 | - | 1: 6.91; 2: 22; 3: 120; 5: 62; 11: 14.08; 25: 930 |  |  |  | Non Complying | Non Complying | - | 8.2 | 105 | 408 |  | 320 | [5 empty] | 42.21 | [13 empty] | 8400
[11 empty] | 12.05.2026 | 140-141 dt. 21.05.2026 | - | 1: 7.8; 2: 37; 3: 128; 5: 45; 11: 7; 25: 78 |  |  |  | Non Complying | Non Complying | - | 6.8 | 130 | 300 |  | 108 | [5 empty] | 13 | [13 empty] | 153000
[11 empty] | 03.06.2026 | 548-549 dt. 11.06.2026 | - | 1: 7.3; 2: 40; 3: 148; 5: 92; 11: 8; 25: 900 |  |  |  | Non Complying | Non Complying | - | 6.6 | 1351 | 364 |  | 115 | [5 empty] | 19 | [13 empty] | 184000
[11 empty] | 06.07.2026 | 823-824 dt. 15.07.2026 |  | 1: 7.1; 2: 9; 3: 48; 5: 18; 11: 4; 14: 0.5; 25: 84; 52: 48; 55: 1110 |  |  |  | Complying | Complying |  | 6.8 | 125 | 336 |  | 264 | [5 empty] | 34 |  |  | 2.7 | [10 empty] | 72000 | [26 empty] | 17 |  |  | 1140
16 | 5 MLD STP, Narnaul, Mahendragarh in 2024
[11 empty] | 14.01.2026 | 2029 dt. 28.01.2026 |  | 1: 7.09; 2: 9.4; 3: 47.8; 5: 19; 11: 8.4; 25: 93 |  |  |  | Complying | Complying |  | 8.46 | 95 | 382.4 |  | 260 | [5 empty] | 43.16 | [13 empty] | 39000
[11 empty] | 04.02.2026 | 2227 dt. 11.02.2026 | 312 | 1: 7.2; 2: 7.5; 3: 40; 5: 17; 11: 7.12; 25: 90 |  |  |  | Complying | Complying | 7.5 | 7.55 | 96 | 387.07 |  | 260 | [5 empty] | 43.83 | [13 empty] | 11000
[11 empty] | 09.03.2026 | 2568 dt. 19.03.2026 | 62.5 | 1: 7.21; 2: 7.6; 3: 36; 5: 16; 11: 6.68; 25: 63 |  |  |  | Complying | Complying | 62.5 | 7.84 | 84 | 376 |  | 235 | [5 empty] | 41.72 | [13 empty] | 5800
[11 empty] | 20.04.2026 | 165 dt. 29.04.2026 | - | 1: 7.25; 2: 8.4; 3: 44; 5: 19; 11: 6.92; 25: 88 |  |  |  | Complying | Complying | - | 7.42 | 120 | 488 |  | 275 | [5 empty] | 39.8 | [13 empty] | 13000
[11 empty] | 12.05.2026 | 138-139 dt. 21.05.2026 | - | 1: 6.9; 2: 8; 3: 40; 5: 17; 11: 6; 25: 72 |  |  |  | Complying | Complying | - | 6.7 | 95 | 376 |  | 160 | [5 empty] | 18 | [13 empty] | 204000
[11 empty] | 03.06.2026 | 550-551 dt. 11.06.2026 | - | 1: 7.1; 2: 8; 3: 44; 5: 16; 11: 3; 25: 86 |  |  |  | Complying | Complying | - | 6.9 | 115 | 312 |  | 260 | [5 empty] | 24 | [13 empty] | 172000
[11 empty] | 06.07.2026 | 821-822 dt. 15.07.2026 |  | 1: 7.3; 2: 8; 3: 40; 5: 16; 11: 4; 14: ND; 25: 80; 52: BDL; 55: 1290 |  |  |  | Complying | Complying |  | 6.7 | 100 | 324 |  | 310 | [5 empty] | 29 |  |  | 2.4 | [10 empty] | 76000 | [26 empty] | 18 |  |  | 1340
17 | (MHD-STP- 005) 6 MLD Near Chinkara Rest House, Rewari Road, Narnaul by ULBD, Aug., 2020 | [9 empty] | 01.12.2020 | 1257-1258 dt. 08.12.2020 | 452700(cusec) | 1: 7; 2: 7; 3: 44; 5: 14; 11: 3.4; 25: 9000; 52: ND; 53: 4700; 54: 18000; 55: 1760 |  |  |  | Complying | Complying | 452701 (cusec) | 6.8 | 105 | 348 |  | 286 | [19 empty] | 47000 | [26 empty] | 12 | 47000 | 610000 | 1840
[12 empty] | Non-Operational and effluent being treated in 7.5 MLD STP Narnual | [122 empty] | 1983 dt. 22.02.2021 | 6.9 | 1810 |  | ND |  |  | 356.1 | 11.2 |  | 0.7 | ND |  | 0.4 | 7.4 | bar: 1 to 11; 25; 52 to 54
18 | 2 MLD STP,Satnali, Mahendragarh by PHED, Jan, 2026 | [9 empty] | 14.01.2026 | 2031 dt. 28.01.2026 | 64.1 | 1: 7.31; 2: 8.2; 3: 39.8; 5: 18; 11: 7; 25: 70 |  |  |  | Complying | Complying |  | 8.08 | 110 | 446.2 |  | 255 | [5 empty] | 40.28 | [13 empty] | 9300
[11 empty] | 03.02.2026 | 2223 dt. 11.02.2026 | - | 1: 7.19; 2: 7.4; 3: 36.2; 5: 16; 11: 8.4; 25: 58 |  |  |  | Complying | Complying | - | 8.23 | 105 | 427.3 |  | 245 | [5 empty] | 32.28 | [13 empty] | 7900
[11 empty] | 24.03.2026 | 2670 dt. 06.04.2026 | - | 1: 7.05; 2: 6.8; 3: 28; 5: 14; 11: -; 25: 49 |  |  |  | Complying | Complying | - | 7.94 | 110 | 448 |  | 260 | [5 empty] | - | [13 empty] | 7000
[11 empty] | 20.04.2026 | 168 dt. 29.04.2026 | - | 1: 7.08; 2: 7.8; 3: 36; 5: 16; 11: -; 25: 84 |  |  |  | Complying | Complying | - | 8.02 | 98 | 368 |  | 225 | [5 empty] | - | [13 empty] | 9300
[11 empty] | 12.05.2026 | 142-143 dt. 21.05.2026 | - | 1: 7.6; 2: 5; 3: 28; 5: 12; 11: ND; 25: 48 |  |  |  | Complying | Complying | - | 6.8 | 110 | 380 |  | 230 | [5 empty] | 12 | [13 empty] | 146000
[11 empty] | 03.06.2026 | 552-553 dt. 10.06.2026 | - | 1: 7.2; 2: 7; 3: 36; 5: 12; 11: 4; 25: 74 |  |  |  | Complying | Complying | - | 6.8 | 100 | 332 |  | 210 | [5 empty] | 32 | [13 empty] | 96000
[11 empty] | 06.07.2026 | 829-830 dt. 15.07.2026 |  | 1: 7.1; 2: 7; 3: 36; 5: 14; 11: ND; 14: ND; 25: 76; 52: BDL; 55: 1370 |  |  |  | Complying | Complying |  | 6.6 | 120 | 364 |  | 264 | [5 empty] | 35 |  |  | 2.9 | [10 empty] | 76000 | [26 empty] | 17 |  |  | 1820
Rewari
19 | (REW-STP-001) 9.5 MLD Kharkhara, Dharuhera , Rewari by PHED in 30.6.2017 |  | 10 | 5.5 to 9.00 | 100 | 10
[11 empty] | 21.01.2026 | 2150 dt. 05.02.2026 |  | 1: 7.82; 2: 8.2; 3: 44; 5: 16; 11: 7.84; 25: 93 |  |  |  | Complying | Complying |  | 7.89 | 98 | 392 |  | 270 | [19 empty] | 29000
[11 empty] | 13.02.2026 | 2334 dt. 20.02.2026 | - | 1: 7.84; 2: 8.6; 3: 48.3; 5: 17; 11: 5.6; 25: 63 |  |  |  | Complying | Complying | 302597 | 8.19 | 78 | 322.5 |  | 195 | [19 empty] | 33000
[11 empty] | 13.02.2026 | 2334 dt. 20.02.2026 | - | 1: 7.84; 2: 8.6; 3: 48.3; 5: 17; 11: 5.6; 25: 63 |  |  |  | Complying | Complying | 302597 | 8.19 | 78 | 322.5 |  | 195 | [19 empty] | 33000
[11 empty] | 17.03.2026 | 2627 dated 30.03.2026 | - | 1: 7.84; 2: 8.6; 3: 48.3; 5: 17; 11: 5.6; 25: 63 |  |  |  | Complying | Complying | 302597.582 | 8.19 | 78 | 322.5 |  | 195 | [5 empty] | 37.12 | [13 empty] | 33000
[11 empty] | 20.04.2026 | 172 dated 29.04.2026 | - | 1: 7.74; 2: 8.2; 3: 40; 5: 14; 11: 7; 25: 79 |  |  |  | Complying | Complying | - | 7.91 | 125 | 424 |  | 320 | [5 empty] | 39.56 | [13 empty] | 21000
[11 empty] | 25.05.2026 | 397-398 dated 01.06.2026 | - | 1: 7.3; 2: 65; 3: 180; 5: 137; 11: -; 25: 1200 |  |  |  | Non Complying | Non Complying | - | 7.9 | 120 | 348 |  | 68 | [5 empty] | - | [13 empty] | 63400
[11 empty] | 03.06.2026 | 559-560 dated 11.06.2026 | - | 1: 7.1; 2: 65; 3: 216; 5: 60; 11: -; 25: 116000 |  |  |  | Non Complying | Non Complying | - | 6.9 | 135 | 476 |  | 198 | [5 empty] | - | [13 empty] | 36000
[11 empty] | 07.07.2026 | 886-887 dt.20.07.2026 |  | 1: 8; 2: 24; 3: 68; 5: 74; 25: 2600; 52: 5; 55: 1312 |  |  |  | Non Complying | Non Complying |  | 7.1 | 105 | 304 |  | 200 | [19 empty] | 68000 | [26 empty] | 6 |  |  | 1389
20 | (REW-STP-002) 3 MLD STP Bawal , Rewari by PHED in 31.3.2014 |  | 30 | 7 to 8.50 | 100 | 50
[11 empty] | 21.01.2026 | 2146 dt.05.02.2026 |  | 1: 7.61; 2: 9.4; 3: 48; 5: 18; 25: 63 |  |  |  | Complying | Complying |  | 8.48 | 98 | 416 |  | 260 | [19 empty] | 3300
[11 empty] | 20.02.2026 | 2443 dated 06.03.2026 | - | 1: 7.56; 2: 8.2; 3: 48; 5: 17; 11: -; 25: 79 |  |  |  | Complying | Complying | 340273.05 | 8.13 | 102 | 416 |  | 235 | [5 empty] | - | [13 empty] | 5800
[11 empty] | 30.03.2026 | 2704 dated 07.04.2026 | - | 1: 7.29; 2: 12; 3: 60; 5: 25; 11: -; 25: 150 |  |  |  | Non Complying | Non Complying | 439854.7 | 8.24 | 98 | 408 |  | 220 | [5 empty] | - | [13 empty] | 6300
[11 empty] | 24.04.2026 | 24-25 dated 01.05.2026 | - | 1: 6.9; 2: 24; 3: 128; 5: 39; 11: 11; 25: 3200 |  |  |  | Non Complying | Non Complying | - | 6.8 | 105 | 320 |  | 296 | [5 empty] | 27 | [13 empty] | 15000
[11 empty] | 29.05.2026 | 501-502 dated 08.06.2026 | - | 1: 6.9; 2: 17; 3: 88; 5: 29; 11: -; 25: 78 |  |  |  | Non Complying | Non Complying | - | 6.5 | 165 | 1160 |  | 194 | [5 empty] | - | [13 empty] | 87100
[11 empty] | 07.06.2026 | 601-602 dt. 18.06.2026 |  | 1: 8.1; 2: 45; 3: 124; 5: 24; 25: 1500 |  |  |  | Non Complying | Non Complying |  | 7.7 | 80 | 324 |  | 90 | [19 empty] | 87100
[11 empty] | 07.07.2026 | 880-881 dt. 20.07.2026 |  | 1: 8.1; 2: 21; 3: 96; 5: 39; 25: 2700; 52: 7; 55: 1920 |  |  |  | Non Complying | Non Complying |  | 7.7 | 95 | 368 |  | 176 | [19 empty] | 84000 | [26 empty] | 15 |  |  | 2150
21 | (REW-STP-003) 6.5 MLD STP Rewari by PHED on 1.10.2014 |  | 30 | 7 to 8.50 | 100 | 50
[11 empty] | 21.01.2026 | 2160 dt. 05.02.2026 |  | 1: 7.65; 2: 70; 3: 312; 5: 85; 11: 18.21; 25: 2900 |  |  |  | Non Complying | Non Complying |  | 7.44 | 104 | 424 |  | 215 | [19 empty] | 13000
[11 empty] | 19.02.2026 | 2441 dated 06.03.2026 | - | 1: 6.64; 2: 125; 3: 496; 5: 310; 11: 24.62; 25: 3900 |  |  |  | Non Complying | Non Complying | - | 7.84 | 140 | 520 |  | 390 | [5 empty] | 53.28 | [13 empty] | 18000
[11 empty] | 30.03.2026 | 2708 dated 07.04.2026 | - | 1: 7.12; 2: 118; 3: 456; 5: 240; 11: 22.23; 25: 4900 |  |  |  | Non Complying | Non Complying | - | 7.74 | 145 | 560 |  | 310 | [5 empty] | 49.13 | [13 empty] | 24000
[11 empty] | 24.04.2026 | 22-23 dated 01.05.2026 | - | 1: 6.7; 2: 105; 3: 320; 5: 196; 11: 9.4; 25: 19000 |  |  |  | Non Complying | Non Complying | - | 6.8 | 135 | 380 |  | 280 | [5 empty] | 38 | [13 empty] | 22000
[11 empty] | 29.05.2026 | 499-500 dated 08.06.2026 | - | 1: 6.7; 2: 85; 3: 196; 5: 58; 11: -; 25: 116000 |  |  |  | Non Complying | Non Complying | - | 6.5 | 165 | 1160 |  | 194 | [5 empty] | - | [13 empty] | 123000
[11 empty] | 07.06.2026 | 599-600 dt. 18.06.2026 |  | 1: 6.9; 2: 55; 3: 220; 5: 62; 25: 5600 |  |  |  | Non Complying | Non Complying |  | 6.6 | 110 | 348 |  | 214 | [19 empty] | 96000
[11 empty] | 07.07.2026 | 882-883 dt.20.07.2026 |  | 1: 7.7; 2: 45; 3: 128; 5: 36; 25: 1600; 52: 5; 55: 3480 |  |  |  | Non Complying | Non Complying |  | 7.6 | 105 | 296 |  | 109 | [19 empty] | 89000 | [26 empty] | 8 |  |  | 3634
22 | (REW-STP-004) 8 MLD STP Rewari by PHED 14.12.2007 |  | 10 | 7.00 TO 8.5 | 50 | 20
[11 empty] | 21.01.2026 | 2161 dt. 05.02.2026 |  | 1: 7.21; 2: 7.4; 3: 36; 5: 15; 11: 7; 25: 63 |  |  |  | Complying | Complying |  | 8.24 | 210 | 720 |  | 360 | [19 empty] | 13000
[11 empty] | 19.02.2026 | 2442 dated 06.03.2026 |  | 1: 7.11; 2: 12; 3: 76; 5: 24; 11: 9.8; 25: 180 |  |  |  | Non Complying | Non Complying | - | 7.49 | 155 | 648 |  | 310 | [5 empty] | 49.28 | [13 empty] | 15000
[11 empty] | 30.03.2026 | 2705 dated 07.04.2026 |  | 1: 7.24; 2: 7.2; 3: 32; 5: 19; 11: 8.2; 25: 93 |  |  |  | Complying | Complying | - | 7.36 | 140 | 556 |  | 270 | [5 empty] | 36.72 | [13 empty] | 15000
[11 empty] | 23.04.2026 | 12-13 dated 01.05.2026 |  | 1: 6.9; 2: 8; 3: 44; 5: 17; 11: 6.7; 25: 90 |  |  |  | Complying | Complying | - | 6.8 | 135 | 500 |  | 385 | [5 empty] | 28 | [13 empty] | 16000
[11 empty] | 30.05.2026 | 515-516 dated 09.06.2026 |  | 1: 6.7; 2: 5; 3: 40; 5: 12; 11: -; 25: 65 |  |  |  | Complying | Complying | - | 6.8 | 370 | 1840 |  | 298 | [5 empty] | - | [13 empty] | 172000
[11 empty] | 07.06.2026 | 593-594 dt. 18.06.2026 |  | 1: 8.4; 2: 8; 3: 48; 5: 17; 25: 72 |  |  |  | Complying | Complying |  | 7.9 | 55 | 312 |  | 204 | [19 empty] | 164000
[11 empty] | 07.07.2026 | 892-893 dt.20.07.2026 |  | 1: 7.6; 2: 8; 3: 48; 5: 16; 25: 74; 52: BDL; 55: 2470 |  |  |  | Complying | Complying |  | 7.4 | 65 | 312 |  | 192 | [19 empty] | 56000 | [26 empty] | 12 |  |  | 1830
23 | (REW-STP-005) 16 MLD STP Rewari by PHED in Sep. 2014 |  | 10 | 6.5 TO 8.00 | 100 | 10
[11 empty] | 22.01.2026 | 2153 dt. 05.02.2026 |  | 1: 7.72; 2: 14; 3: 68; 5: 26; 11: 11.2; 25: 150 |  |  |  | Non Complying | Non Complying |  | 8.24 | 210 | 720 |  | 360 | [19 empty] | 13000
[11 empty] | 19.02.2026 | 2440 dated 06.03.2026 | - | 1: 7.06; 2: 18; 3: 88; 5: 45; 11: 14.01; 25: 210 |  |  |  | Non Complying | Non Complying | - | 7.49 | 155 | 648 |  | 310 | [5 empty] | 49.28 | [13 empty] | 15000
[11 empty] | 30.03.2026 | 2707 dated 07.04.2026 | - | 1: 7.24; 2: 14; 3: 68; 5: 29; 11: 13.6; 25: 190 |  |  |  | Non Complying | Non Complying | - | 7.83 | 140 | 556 |  | 270 | [5 empty] | 36.72 | [13 empty] | 15000
[11 empty] | 23.04.2026 | 14-15 dated 01.05.2026 | - | 1: 6.9; 2: 16; 3: 80; 5: 25; 11: 9; 25: 220 |  |  |  | Non Complying | Non Complying | - | 6.8 | 130 | 480 |  | 2100 | [5 empty] | 31 | [13 empty] | 15000
[11 empty] | 30.05.2026 | 513-514 dated 09.06.2026 | - | 1: 7.5; 2: 17; 3: 88; 5: 12; 11: -; 25: 760 |  |  |  | Non Complying | Non Complying | - | 7.2 | 410 | 1320 |  | 322 | [5 empty] | - | [13 empty] | 183500
[11 empty] | 07.06.2026 | 595-596 dt. 18.06.2026 |  | 1: 8.1; 2: 26; 3: 112; 5: 45; 25: 2400 |  |  |  | Non Complying | Non Complying |  | 7.6 | 65 | 372 |  | 88 | [19 empty] | 140000
[11 empty] | 07.07.2026 | 890-891 dt.20.07.2026 |  | 1: 7.7; 2: 25; 3: 88; 5: 28; 25: 1900; 52: BDL; 55: 1820 |  |  |  | Non Complying | Non Complying |  | 7.4 | 120 | 336 |  | 192 | [19 empty] | 64000 | [26 empty] | 8 |  |  | 1820
24 | (REW-STP-006) 3 MLD STP, Kosli , Rewari by PHED in 31.4.2016 |  | 30 | 7.5 to 8.5 | 100 | 40
[11 empty] | 21.01.2026 | 2151 dt. 05.02.2026 |  | 1: 7.81; 2: 62; 3: 256; 5: 78; 11: 12.6; 25: 930 |  |  |  | Non Complying | Non Complying |  | 8.13 | 110 | 456 |  | 250 | [5 empty] | 31.86 | [13 empty] | 13000
[11 empty] | 13.02.2026 | 2333 dt. 20.02.2026 |  | 1: 7.55; 2: 55; 3: 225.7; 5: 60; 11: 14.01; 25: 880 |  |  |  | Non Complying | Non Complying |  | 8.36 | 85 | 346.7 |  | 220 | [5 empty] | 30.82 | [13 empty] | 15000
[11 empty] | 30.03.2026 | 2709 dated 07.04.2026 | - | 1: 7.42; 2: 68; 3: 256; 5: 72; 11: 18.21; 25: 790 |  |  |  | Non Complying | Non Complying | - | 7.96 | 94 | 392 |  | 245 | [5 empty] | 34.92 | [13 empty] | 18000
[11 empty] | 24.04.2026 | 18-19 dated 01.05.2026 | - | 1: 6.6; 2: 70; 3: 204; 5: 110; 11: 9; 25: 9000 |  |  |  | Non Complying | Non Complying | - | 6.6 | 95 | 240 |  | 160 | [5 empty] | 22 | [13 empty] | 13000
[11 empty] | 22.05.2026 | 328-329 dated 01.06.2026 | - | 1: 7; 2: 24; 3: 88; 5: 28; 11: -; 25: 1400 |  |  |  | Non Complying | Non Complying | - | 7 | 115 | 432 |  | 66 | [5 empty] | - | [13 empty] | 81000
[11 empty] | 04.06.2026 | 576-577 dated 11.06.2026 | - | 1: 6.9; 2: 55; 3: 156; 5: 58; 11: -; 25: 960 |  |  |  | Non Complying | Non Complying | - | 6.8 | 115 | 512 |  | 172 | [5 empty] | - | [13 empty] | 112000
[11 empty] | 02.07.2026 | 803-804 dt.11.07.2026 |  | 1: 7.8; 2: 45; 3: 136; 5: 50; 25: 8500; 52: BDL; 55: 3200 |  |  |  | Non Complying | Non Complying |  | 7.4 | 110 | 392 |  | 152 | [19 empty] | 14000 | [26 empty] | 7 |  |  | 2050
25 | (REW-STP-007) 5 MLD STP , HUDA, Sec-6, Dharuhera in 2020
[11 empty] | 21.01.2026 | 2152 dt. 05.02.2026 | - | 1: 7.24; 2: 8.5; 3: 48; 5: 19; 11: 8.48; 25: 93 |  |  |  | Complying | Complying |  | 7.69 | 90 | 376 |  | 215 | [5 empty] | 144778 | [13 empty] | 21000
[11 empty] | 13.02.2026 | 2332 dt. 20.02.2026 | - | 1: 7.25; 2: 7.4; 3: 40.3; 5: 12; 11: 6.56; 25: 70 |  |  |  | Complying | Complying | 149460 | 7.88 | 102 | 419.3 |  | 245 | [5 empty] | 36.54 | [13 empty] | 27000
[11 empty] | 13.02.2026 | 2332 dt. 20.02.2026 | - | 1: 7.25; 2: 7.4; 3: 40.3; 5: 12; 11: 6.56; 25: 70 |  |  |  | Complying | Complying | 149460 | 7.88 | 102 | 419.3 |  | 245 | [5 empty] | 36.54 | [13 empty] | 27000
[11 empty] | 17.03.2026 | 2625 dated 30.03.2026 | - | 1: 7.31; 2: 6.8; 3: 36; 5: 14; 11: 7.16; 25: 84 |  |  |  | Complying | Complying | - | 7.96 | 98 | 408 |  | 210 | [5 empty] | 31.92 | [13 empty] | 31000
[11 empty] | 20.04.2026 | 173 dated 29.04.2026 | - | 1: 7.9; 2: 8.8; 3: 48; 5: 17; 11: 8.28; 25: 93 |  |  |  | Complying | Complying | - | 7.84 | 110 | 456 |  | 265 | [5 empty] | 38.74 | [13 empty] | 27000
[11 empty] | 25.05.2026 | 399-400 dated 01.06.2026 | - | 1: 7.1; 2: 6; 3: 44; 5: 17; 11: -; 25: 67 |  |  |  | Complying | Complying | - | 7.2 | 105 | 364 |  | 28 | [5 empty] | - | [13 empty] | 45000
[11 empty] | 03.06.2026 | 561-562 dt. 11.06.2026 |  | 1: 7.5; 2: 4; 3: 32; 5: 10; 25: 78 |  |  |  | Complying | Complying |  | 7.4 | 110 | 432 |  | 130 | [19 empty] | 87000
[11 empty] | 07.07.2026 | 884-885 dt.20.07.2026 |  | 1: 7.9; 2: 7; 3: 32; 5: 12; 25: 88; 52: BDL; 55: 1674 |  |  |  | Complying | Complying |  | 7.6 | 115 | 316 |  | 206 | [19 empty] | 76000 | [26 empty] | 13 |  |  | 3480
Ambala
26 | (AMB-STP-013) 4 MLD STP, PHED, Barara, Ambala in 30.11.2019 |  | 10 | 5.5-9 | 100 | 10
[11 empty] | 06.01.2026 | 4217 dt. 15.01.2026 |  | 1: 7.15; 2: 5.8; 3: 36; 5: 12; 11: ND |  |  |  | Complying | Complying
[11 empty] | 02.02.2026 | 4401, 10.02.2026 | 78.062 | 1: 7.52; 2: 7.4; 3: 48; 5: 14; 11: ND; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 10.03.2026 | 4690, 24.03.2026 | 66.73 | 1: 7.72; 2: 4.8; 3: 28; 5: 9; 11: _; 25: ND |  |  |  | Complying | Complying
[11 empty] | 03.04.2026 | 31, 17.04.2026 | 64.8 | 1: 7.73; 2: 7.5; 3: 40; 5: 13; 11: ND; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 20.05.2026 | 293, 01.06.2026 | _ | 1: 8.45; 2: 7.2; 3: 40; 5: 13; 11: 4.96; 25: 70 |  |  |  | Complying | Complying
[11 empty] | 03.06.2026 | 405, 15.06.2026 | 57.28 | 1: 8.4; 2: 7.2; 3: 36; 5: 8; 11: 2.41; 25: 50 |  |  |  | Complying | Complying
[11 empty] | 01.07.2026 | 552 dt. 08.07.2026 |  | 1: 8.2; 2: 6.2; 3: 32; 5: 9; 11: 4.2; 15: 0.49; 25: 70; 52: BDL(DL=02); 55: 661 |  |  |  | Complying | Complying
Karnal
27 | (KRN-STP-010) 5 MLD STP Assandh, Karnal by PHED in 2.4.2014 | Deptt. | 10 | 7-8.00 | 50 | 10
[11 empty] | 06.01.2026 | 4199 dt. 15.01.2026 |  | 1: 7.22; 2: 17; 3: 80; 5: 35; 11: 8.22 |  |  |  | Non complying | Non complying |  | 6.72 | 120 | 428 |  | 228 | [5 empty] | 14.56
[11 empty] | 10.02.2026 | 4467 dt. 23.02.2026 | 112746.9 | 1: 7.79; 2: 13; 3: 64; 5: 27; 11: 9.28; 25: 600 |  |  |  | Non complying | Non complying | 197456.8 | 7.39 | 125 | 428 |  | 182 | [5 empty] | 13.2
[11 empty] | 12.03.2026 | 4706 dt. 25.03.2026 |  | 1: 8.31; 2: 7.8; 3: 44; 5: 12; 11: 1.58; 25: 50 |  |  |  | Complying | Complying |  | 7.65 | 190 | 636 |  | 214 | [5 empty] | 14.58
[11 empty] | 02.04.2026 | 26 dt. 17.04.2026 |  | 1: 7.97; 2: 7.8; 3: 48; 5: 15; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 7.5 | 135 | 480 |  | 285 | [5 empty] | 15.78
[11 empty] | 11.05.2026 | 236 dt. 20.05.2026 |  | 1: 8.23; 2: 12; 3: 64; 5: 24; 11: 1.78; 25: 70 |  |  |  | Non complying | Non complying |  | 8.13 | 98 | 324 |  | 192 | [5 empty] | 14.56
[11 empty] | 05.06.2026 | 438 dt. 16.06.2026 |  | 1: 8.02; 2: 8.5; 3: 44; 5: 16; 25: 80 |  |  |  | Complying | Complying |  | 7.83 | 135 | 452 |  | 255 | [5 empty] | -
| July, 2026 1st Phase | [9 empty] | 04.07.2026 | 603 dt. 13.07.2026 |  | 1: 7.08; 2: 7.6; 3: 48; 5: 16; 25: 90; 52: BDL |  |  |  | Complying | Complying |  | 7.77 | 96 | 308 |  | 122 | [19 empty] | 1.26X105 | [26 empty] | 17.5
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | 725 dt. 05.08.2026 |  | 1: 7.66; 2: 5.8; 3: 24; 5: 7; 6: 200; 7: 72.97; 9: 93.77; 12: ND; 13: ND; 14: ND; 16: ND; 17: ND; 18: 56.8; 19: 68; 20: 88; 23: 222; 24: 156; 25: 50; 28: 1.96; 31: BDL(DL=0.001); 32: BDL(DL=0.230); 33: ND; 34: BDL(DL=0.07); 35: BDL(DL=0.163); 36: BDL(DL=0.032); 37: BDL(DL=0.01); 38: BDL(DL=0.001); 42: BDL(DL=0.5243); 43: BDL(DL=0.001); 52: BDL(DL=02); 55: 370 |  |  |  | Complying | Complying |  | 7.73 | 120 | 404 |  | 193 | 798 | 103.96 |  | 331.53 |  |  | 13.54 | 10.92 | 2.34 |  | 3.6 | ND | 86.4 | 154 | 102 |  |  | 384 | 256 | 1.22X105 |  |  | 2.33 |  |  | BDL(DL=0.001) | BDL(DL=0.230) | 1.9286 | BDL(DL=0.07) | BDL(DL=0.163) | BDL(DL=0.032) | BDL(DL=0.01) | BDL(DL=0.001) |  |  |  | BDL(DL=0.5243) | BDL(DL=0.001) | [8 empty] | 21 |  |  | 1454
Gurgaon North
28 | (GRN-STP-004) 6 MLD STP Sohna Gurgaon (North) by PHED in 1.3.2014 |  | 30 | 7-8.5 | 100 | 50
[11 empty] | 14.01.2026 | 2010 dt. 28.01.2026 |  | 1: 7.24; 2: 80; 3: 326.6; 5: 210; 11: 18.02; 25: 5800; 52: 4.4 |  |  |  | Non complying | Non complying |  | 7.83 | 125 | 494.01 |  | 290 | [5 empty] | 43.14 | [13 empty] | 9300 | [26 empty] | 9.6
[11 empty] | 23.02.2026 | 2466 dt. 06.03.2026 |  | 1: 7.41; 2: 62; 3: 288; 5: 75; 11: 15.84; 25: 330; 52: BDL |  |  |  | Non complying | Non complying |  | 7.72 | 92 | 384 |  | 255 | [5 empty] | 36.12 | [13 empty] | 11000 | [26 empty] | 12.4
[11 empty] | 12.03.2026 | 2610 dt. 25.03.2026 |  | 1: 7.11; 2: 52; 3: 248; 5: 95; 11: 18.72; 25: 790; 52: 5.2 |  |  |  | Non complying | Non complying |  | 7.82 | 85 | 344 |  | 270 | [5 empty] | 31.64 | [13 empty] | 9300 | [26 empty] | 9.6
[11 empty] | 20.04.2026 | 176 dt. 30.04.2026 |  | 1: 7.4; 2: 44; 3: 164; 5: 62; 11: 14.56; 25: 630; 52: 6.2 |  |  |  | Non complying | Non complying |  | 7.91 | 110 | 416 |  | 280 | [5 empty] | 34.42 | [13 empty] | 8400 | [26 empty] | 11.8
[11 empty] | 25.05.2026 | 383-384 dt. 01.06.2026 |  | 1: 7.2; 2: 14; 3: 72; 5: 7; 25: 67; 52: BDL |  |  |  | Non complying | Non complying |  | 7.3 | 115 | 372 |  | 67 | [19 empty] | 210000 | [26 empty] | 17
[11 empty] | 10.06.2026 | 647-648 dt.18.06.2026 |  | 1: 6.9; 2: 27; 3: 124; 5: 108; 11: 15; 25: 6800; 52: 13 |  |  |  | Non complying | Non complying |  | 6.4 | 115 | 332 |  | 196 | [5 empty] | 32 | [13 empty] | 72000 | [26 empty] | 24
Gurgaon South
29 | (GRS-STP-007) 4.5 MLD STP Pataudi Gurgaon by PHED in 30.6.2017 (South) |  | 20 | 7-8.5 | 100 | 40
[11 empty] | 21.01.2026 | 2132 dt. 04.02.2026 |  | 1: 7.26; 2: 45; 3: 224; 5: 75; 11: 14.01; 25: 780; 52: 4.4 |  |  |  | Non complying | Non complying |  | 7.88 | 108 | 456 |  | 245 | [5 empty] | 42.84 | [13 empty] | 9300 | [26 empty] | 10.2
[11 empty] | 23.02.2026 | 2453 dt. 06.03.2026 |  | 1: 7.35; 2: 52; 3: 248; 5: 92; 11: 17.22; 25: 630; 52: 5.8 |  |  |  | Non complying | Non complying |  | 7.96 | 115 | 488 |  | 230 | [5 empty] | 50.12
[11 empty] | 10.03.2026 | 2579 dt. 20.03.2026 |  | 1: 7.09; 2: 48; 3: 196; 5: 85; 11: 15.64; 25: 840; 52: 4.8 |  |  |  | Non complying | Non complying |  | 8.32 | 172 | 440 |  | 275 | [5 empty] | 48.12 | [13 empty] | 930 | [26 empty] | 9.6
[11 empty] | 20.04.2026 | 180 dt. 30.04.2026 |  | 1: 7.32; 2: 50; 3: 204; 5: 72; 11: 18.01; 25: 930; 52: 5.2 |  |  |  | Non complying | Non complying |  | 7.49 | 140 | 392 |  | 230 | [5 empty] | 41.43 | [13 empty] | 7900 | [26 empty] | 10.4 |  |  | 1308
[11 empty] | 12.05.2026 | 127-128 dt. 21.05.2026 |  | 1: 7.6; 2: 35; 3: 140; 5: 40; 11: 2.6; 25: 15000; 55: 1437 |  |  |  | Non complying | Non complying |  | 6.8 | 145 | 356 |  | 284 | [5 empty] | 2.6 | [13 empty] | 130000
[11 empty] | 10.06.2026 | 643 dt. 18.06.2026 |  | 1: 6.4; 2: 95; 3: 324; 5: 216; 11: 24; 25: 32000; 52: 19 |  |  |  | Non complying | Non complying
| July, 2026 1st Phase | [9 empty] | 07.07.2026 | 852 dt. 16.07.2026 |  | 1: 7.9; 2: 70; 3: 308; 5: 222; 11: 29; 25: 62000; 52: 24 |  |  |  | Non complying | Non complying
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 1077 dt. 30.07.2026 |  | 1: 7.2; 2: 65; 3: 292; 5: 286; 6: 721; 9: 390; 10: ND; 11: 21; 12: 18; 13: 12; 14: 1.5; 15: 1.4; 16: ND; 17: ND; 19: 220; 20: 320; 24: 520; 25: 2400; 28: ND; 31: ND; 33: ND; 35: ND; 36: ND; 42: ND; 52: 18; 55: 1442 |  |  |  | Non complying | Non complying
[11 empty] | 06.08.2026 | 1416 dt. 14.08.2026 |  | 1: 7; 2: 130; 3: 372; 5: 302; 6: 768; 9: 412; 10: BDL; 11: 34; 12: 24; 13: 18; 14: 1.8; 15: 1.6; 16: BDL; 17: BDL; 19: 235; 20: 340; 24: 555; 25: 12000; 28: BDL; 31: BDL; 33: BDL; 35: BDL; 36: BDL; 42: BDL; 52: 12; 55: 1520 |  |  |  | Non complying | Non complying
30 | (GRS-STP-008) 3 MLD STP at Farrukhnagar , Gurugram by PHED in 30.06.2018 (South) |  | 10 | 6.5-9.0 | 50 | 20
[11 empty] | 15.01.2026 | 2058 dt. 01.02.2026 |  | 1: 7.34; 2: 8.2; 3: 48; 5: 17; 11: 8.4; 25: 70; 52: BDL*(DL**=4); 55: 1290 |  |  |  | Complying | Complying |  | 7.72 | 110 | 424 |  | 175 | [5 empty] | 34.26 | [13 empty] | 8400 | [26 empty] | 7.6 |  |  | 4560
[11 empty] | 23.02.2026 | 2452 dt. 06.03.2026 |  | 1: 7.26; 2: 78; 3: 304; 5: 180; 11: 18.61; 25: 1100; 52: 5.2 |  |  |  | Non complying | Non complying |  | 7.81 | 95 | 384 |  | 275 | [5 empty] | 28.02 | [13 empty] | 8400 | [26 empty] | 6.8
[11 empty] | 10.03.2026 | 2578 dt. 20.03.2026 |  | 1: 6.95; 2: 80; 3: 328; 5: 195; 11: 16.84; 25: 1800; 52: 6.6 |  |  |  | Non complying | Non complying
[11 empty] | 20.04.2026 | 179 dt. 30.04.2026 |  | 1: 6.55; 2: 82; 3: 432; 5: 210; 11: 20.12; 25: 1300; 52: 6.8 |  |  |  | Non complying | Non complying
[11 empty] | 08.05.2026 | 103-104 dt. 18.05.2026 |  | 1: 7.8; 2: 7; 3: 44; 5: 13; 11: 5; 25: 92 |  |  |  | Complying | Complying |  | 6.5 | 120 | 580 |  | 344 | [5 empty] | 40 | [13 empty] | 137500
[11 empty] | 10.06.2026 | 644-645 dt. 18.06.2026 |  | 1: 7.1; 2: 8; 3: 44; 5: 14; 11: 3; 25: 92; 52: BDL; 55: 1240 |  |  |  | Complying | Complying |  | 6.9 | 105 | 348 |  | 186 | [5 empty] | 29 | [13 empty] | 88000 | [26 empty] | 19 |  |  | 1760
| July, 2026 1st Phase | [9 empty] | 07.07.2026 | 853-854 dt. 16.07.2026 |  | 1: 7.8; 2: 8; 3: 40; 5: 8; 11: 4; 25: 84; 52: BDL; 55: 1640 |  |  |  | Complying | Complying |  | 7.9 | 85 | 396 |  | 154 | [5 empty] | 31 | [13 empty] | 76000 | [26 empty] | 24 |  |  | 1980
| July, 2026 2nd Phase | [9 empty] | 21.07.2026 | 1067-1068 dt. 30.07.2026 |  | 1: 6.5; 2: 7; 3: 32; 5: 12; 6: 1020; 9: 60; 10: ND; 11: 3.5; 12: ND; 13: ND; 14: ND; 15: ND; 16: ND; 17: ND; 19: 40; 20: 70; 24: 110; 25: 76; 28: ND; 31: ND; 33: ND; 35: ND; 36: ND; 42: ND; 52: ND; 55: 2040 |  |  |  | Complying | Complying |  | 6.3 | 80 | 376 |  | 788 | 1280 |  |  | 240 | ND | 12.5 | 6.5 | 0.5 | 2.1 | 2.5 | ND | ND |  | 140 | 310 |  |  |  | 450 | 81000 |  |  | ND |  |  | ND |  | ND |  | ND | ND | [5 empty] | ND | [9 empty] | 11.4 |  |  | 2340
[11 empty] | 06.08.2026 | 1414-1415 dt. 14.08.2026 |  | 1: 7.5; 2: 5; 3: 36; 5: 16; 6: 776; 9: 68; 10: BDL; 11: 2.9; 12: ND; 13: ND; 14: BDL; 15: ND; 16: BDL; 17: BDL; 19: 44; 20: 88; 24: 142; 25: 82; 28: BDL; 31: BDL; 33: BDL; 35: BDL; 36: BDL; 42: BDL; 52: BDL; 55: 1420 |  |  |  | Complying | Complying |  | 7.1 | 115 | 328 |  | 304 | 812 |  |  | 208 | BDL | 13.5 | 32.5 | 21 | 2.9 | 2.5 | BDL | BDL |  | 112 | 258 |  |  |  | 370 | 62000 |  |  | BDL |  |  | BDL |  | BDL |  | BDL | BDL | [5 empty] | BDL | [9 empty] | 8 |  |  | 1570
31 | (GRS-STP-009) 5.5 MLD STP at Haily Mandi , Gurugram by PHED in 30.06.2018 (South)
[11 empty] | 21.01.2026 | 2133 dt. 04.02.2026 |  | 1: 7.38; 2: 38; 3: 188; 5: 60; 11: 11.6; 25: 330; 52: BDL*(DL**=4); 55: 2420 |  |  |  | Non complying | Non complying |  | 7.76 | 98 | 392 |  | 205 | [5 empty] | 31.82 | [13 empty] | 7900 | [26 empty] | 7.8 |  |  | 5160
[11 empty] | 23.02.2026 | 2452 dt. 06.03.2026 |  | 1: 7.26; 2: 78; 3: 304; 5: 180; 11: 18.61; 25: 1100; 52: 5.2 |  |  |  | Non complying | Non complying |  | 7.81 | 95 | 384 |  | 275 | [5 empty] | 28.02 | [13 empty] | 8400 | [26 empty] | 6.8
[11 empty] | 10.03.2026 | 2578 dt. 20.03.2026 |  | 1: 6.95; 2: 80; 3: 328; 5: 195; 11: 16.84; 25: 1800; 52: 6.6 |  |  |  | Non complying | Non complying
[11 empty] | 20.04.2026 | 179 dt. 30.04.2026 |  | 1: 6.55; 2: 82; 3: 432; 5: 210; 11: 20.12; 25: 1300; 52: 6.8 |  |  |  | Non complying | Non complying
[11 empty] | 12.05.2026 | 131 dt. 21.05.2026 |  | 1: 6.8; 2: 120; 3: 348; 5: 54; 11: ND; 25: 196000 |  |  |  | Non complying | Non complying
[11 empty] | 10.06.2026 | 646 dt. 18.06.2026 |  | 1: 6.8; 2: 120; 3: 376; 5: 272; 11: 35; 25: 62000; 52: 24; 55: 1980 |  |  |  | Non complying | Non complying
| July, 2026 1st Phase | [9 empty] | 07.07.2026 | 855 dt. 16.07.2026 |  | 1: 7.4; 2: 110; 3: 318; 5: 156; 11: 27; 25: 92000; 52: 19; 55: 1520 |  |  |  | Non complying | Non complying
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 1078 dt. 30.07.2026 |  | 1: 7.4; 2: 135; 3: 336; 5: 198; 6: 855; 9: 460; 10: 2.4; 11: 24; 12: 17; 13: 15; 14: 1.5; 15: 1.8; 16: ND; 17: ND; 19: 240; 20: 380; 24: 620; 25: 75000; 28: ND; 31: ND; 33: ND; 35: ND; 36: ND; 42: ND; 52: 16; 55: 1705 |  |  |  | Non complying | Non complying
[11 empty] | 06.08.2026 | 1413 dt. 14.08.2026 |  | 1: 8.9; 2: 100; 3: 308; 5: 280; 6: 795; 9: 342; 10: BDL; 11: 29; 12: 40.6; 13: 12.2; 14: 3.6; 15: 1.5; 16: BDL; 17: BDL; 19: 134; 20: 376; 24: 510; 25: 42000; 28: BDL; 31: BDL; 33: BDL; 35: BDL; 36: BDL; 42: BDL; 52: 9; 55: 1570 |  |  |  | Non complying | Non complying
Jind
32 | (KTL-STP-008) 4 MLD STP Julana ,Jind by PHED in 1.4.2016 |  | 30 | 7.0-8.5 | 250 | 100
[11 empty] | 07.01.2026 | 4239 dt. 20.01.2026 |  | 1: 8.06; 2: 7.8; 3: 48; 5: 15; 11: ND |  |  |  | Complying | Complying |  | 7.1 | 140 | 480 |  | 235 | [5 empty] | 13.29
[11 empty] | 11.02.2026 | 4487 dt. 24.02.2026 | 70208.4 | 1: 8; 2: 5.5; 3: 32; 5: 9; 11: ND; 25: 70 |  |  |  | Complying | Complying | 495877.7 | 7.6 | 92 | 320 |  | 158 | [5 empty] | 15.82
[11 empty] | 18.03.2026 | 4738 dt. 02.04.2026 | 73290.8 | 1: 8.76; 2: 6.7; 3: 32; 5: 12; 11: ND; 25: 50 |  |  |  | Complying | Complying |  | 7.97 | 105 | 340 |  | 175 | [5 empty] | 13.79 | [13 empty] | -
[11 empty] | 16.04.2026 | 135 dt. 29.04.2026 |  | 1: 7.9; 2: 7.4; 3: 44; 5: 7; 11: 3.38; 25: 90 |  |  |  | Complying | Complying | - | 8.16 | 160 | 560 |  | 208 | [5 empty] | 17.34 | [13 empty] | -
[11 empty] | 07.05.2026 | 61-62-A dated 13.05.2026 | 16.43 | 1: 7.3; 2: 7.4; 3: 28; 5: 14; 25: 68 |  |  |  | Complying | Complying | 4.26 | 7.6 | 142 | 356 |  | 218
[11 empty] | 18.06.2026 | 340-341- A dt. 23.06.2026 | Not working | 1: 7.1; 2: 9.2; 3: 24; 5: 18; 25: 62 |  |  |  | Complying | Complying |  | 7.8 | 138 | 352 |  | 212 | [19 empty] | 7.6 X 10⁴
| July, 2026 1st Phase | [9 empty] | 09.07.2026 | 483-484 A dt. 15.07.2026 |  | 1: 7.6; 2: 8.2; 3: 28; 5: 14; 25: 56; 52: BDL |  |  |  | Complying | Complying |  | 8.4 | 124 | 288 |  | 248 | [19 empty] | 4.8X 10⁴ | [26 empty] | 12
| July, 2026 2nd Phase | [9 empty] | 20.07.2026 | 553-554-A dt. 04.08.2026 |  | 1: 7.8; 2: 7.2; 3: 32; 5: 12; 6: 432; 7: 158.2; 8: 195.2; 9: 142.7; 18: 36; 19: 24.3; 20: 36.1; 23: 160; 24: 190; 25: 62; 28: 6.5; 29: 3.4; 31: 0.9; 52: BDL(DL=4); 55: 1450 |  | 0.7 |  | Complying | Complying |  | 8.1 | 120 | 248 |  | 148 | 975 | 481.8 | 341.6 | 248.7 | [8 empty] | 174 | 82.6 | 120.2 |  |  | 280 | 640 | 4.8X 10⁴ |  |  | 17.3 | 6.4 |  | 2.1 | [20 empty] | 42 |  |  | 2982 |  | 1.7
Hisar
33 | (HSR-STP-006) 6.5 MLD STP Uklana, Hisar by PHED in 1.9.2017 |  | 10 | 5.5-9.0 | 100 | 10
[11 empty] | 28.01.2026 | 4375 dt. 09.02.2026 | 4.1 | 1: 7.93; 2: 7.5; 3: 48; 5: 15; 11: ND |  |  |  | Complying | Complying | 4.22 | 6.68 | 145 | 492 |  | 232 | [5 empty] | 15.28
[11 empty] | 25.02.2026 | 4600 dt. 11.03.2026 |  | 1: 7.99; 2: 8.5; 3: 40; 5: 18; 11: 8.39; 25: 90 |  |  |  | Complying | Complying |  | 7.26 | 120 | 428 |  | 184 | [5 empty] | 15.68
[11 empty] | 27.03.2026 | 4780 dt. 08.04.2026 | 4.82 | 1: 7.79; 2: 8.6; 3: 48; 5: 15; 11: ND; 25: 90 |  |  |  | Complying | Complying | 4.98 | 7.05 | 220 | 688 |  | 276 | [5 empty] | 15.76
[11 empty] | 23.04.2026 | 7-8A dt. 28.04.2026 |  | 1: 7.4; 2: 8; 3: 48; 5: 16; 25: 80 |  |  |  | Complying | Complying |  | 7.1 | 186 | 464 |  | 262
[11 empty] | 15.05.2026 | 149-150A dt. 22.05.2026 |  | 1: 7.7; 2: 8.6; 3: 42; 5: 14; 11: 12; 25: 82 |  |  |  | Complying | Complying |  | 7.6 | 100 | 232 |  | 198 | [5 empty] | 28 | [13 empty] | 96000
[11 empty] | 10.06.2026 | 309-310A dt. 16.06.2026 |  | 1: 7.8; 2: 8.4; 3: 32; 5: 12; 11: 8.2; 25: 80 |  |  |  | Complying | Complying |  | 8.8 | 108 | 376 |  | 212 | [5 empty] | 28.2 | [13 empty] | 42000
[11 empty] | 06.07.2026 | 421-422A dt. 14.07.2026 |  | 1: 7.2; 2: 7.8; 3: 24; 5: 11; 11: 14; 25: 64; 52: BDL |  |  |  | Complying | Complying |  | 8.2 | 118 | 360 |  | 336 | [5 empty] | 26 | [13 empty] | 38000 | [26 empty] | 26
[11 empty] | 17.07.2026 | 513-14 dt 30.07.2026 |  | 1: 7.9; 2: 27; 3: 88; 5: 19; 25: 96; 52: 6 |  |  |  | Non complying | Non complying |  | 7.6 | 148 | 368 |  | 318 | [19 empty] | 38000 | [26 empty] | 32
[11 empty] | 03.08.2026 | 637 dt. 18.08.2026 |  | 1: 7.4; 2: 7.8; 3: 36; 5: 18; 25: 64; 52: BDL |  |  |  | Complying | Complying |  | 8.5 | 102 | 364 |  | 198 | [19 empty] | 48000 | [26 empty] | 28
34 | (HSR-STP-007) 6.5 MLD STP Hansi , Hisar by PHED in 31.05.2019 |  | 10 | 6.5 to 9 | 50 | 20
[11 empty] | 28.01.2026 | 4379 dt. 09.02.2026 | 3.6 | 1: 7.48; 2: 6.2; 3: 40; 5: 12; 11: ND |  |  |  | Complying | Complying | 3.98 | 7.25 | 130 | 420 |  | 268 | [5 empty] | 14.28
[11 empty] | 20.02.2026 | 4566 dt. 10.03.2026 |  | 1: 7.08; 2: 64; 3: 244; 5: 156; 11: 15.78; 25: 1100 |  |  |  | Non complying | Non complying
[11 empty] | 27.03.2026 | 4785 dt. 08.04.2026 | 5.98 | 1: 7.69; 2: 8.6; 3: 48; 5: 11; 11: 3.88; 25: 90 |  |  |  | Complying | Complying | 6 | 7.46 | 145 | 460 |  | 224 | [5 empty] | 19.32
[11 empty] | 28.04.2026 | 13-14A dt. 05.05.2026 |  | 1: 7.4; 2: 8; 3: 18; 5: 16; 25: 72 |  |  |  | Complying | Complying |  | 7 | 150 | 532 |  | 456
[11 empty] | 27.05.2026 | 216-217A dt. 04.06.2026 |  | 1: 7.8; 2: 9; 3: 48; 5: 18; 11: ND; 25: 90 |  |  |  | Complying | Complying |  | 8.6 | 164 | 440 |  | 246 | [5 empty] | ND | [13 empty] | 28000
[11 empty] | 10.06.2026 | 319-320A dt. 16.06.2026 |  | 1: 7.8; 2: 8.2; 3: 36; 5: 18; 11: 8.2; 25: 72 |  |  |  | Complying | Complying |  | 8.4 | 102 | 408 |  | 224 | [5 empty] | 32.4 | [13 empty] | 58000
[11 empty] | 01.07.2026 | 388-389-A dt.07.07.2026 |  | 1: 8.1; 2: 8.6; 3: 32; 5: 12; 25: 56 |  |  |  | Complying | Complying |  | 7.8 | 82 | 208 |  | 146 | [19 empty] | 4.2 X 10⁴
[11 empty] | 01.07.2026 | 388-389-A dt.07.07.2026 |  | 1: 8.1; 2: 8.6; 3: 32; 5: 12; 25: 56 |  |  |  | Complying | Complying |  | 82 | 208 | 7.8 |  | 146 | [19 empty] | 4.2 X 10⁴
[11 empty] | 16.07.2026 | 509-10 dt 30.07.2026 |  | 1: 7.9; 2: 26; 3: 88; 5: 46; 25: 2100; 52: 8 |  |  |  | Non complying | Non complying |  | 7.8 | 102 | 264 |  | 198 | [19 empty] | 65000 | [26 empty] | 40
[11 empty] | 07.08.2026 | 723 dt. 21.08.2026 |  | 1: 8.2; 2: 102; 3: 198; 5: 182; 25: 36000; 52: BDL |  |  |  | Non complying | Non complying
35 | (HSR-STP-008) 6 MLD STP Dhani Gram ,Barwala, Hisar by PHED in 9.12.2014 |  | 20 | 5.5-9.0 | 100 | <40
[11 empty] | 28.01.2026 | 4374 dt. 09.02.2026 | 5.1 | 1: 7.25; 2: 6.8; 3: 40; 5: 12; 11: ND |  |  |  | Complying | Complying | 5.22 | 7.7 | 120 | 396 |  | 138 | [5 empty] | 13.47
[11 empty] | 25.02.2026 | 4601 dt. 11.03.2026 |  | 1: 7.83; 2: 9.5; 3: 60; 5: 26; 11: 4.26; 25: 400 |  |  |  | Non complying | Non complying |  | 7.7 | 120 | 432 |  | 196 | [5 empty] | 14.32
[11 empty] | 27.03.2026 | 4783 dt. 08.04.2026 | 5.42 | 1: 8.04; 2: 26; 3: 116; 5: 28; 11: 2.98; 25: 200 |  |  |  | Non complying | Non complying | 5.52 | 7.87 | 140 | 476 |  | 208 | [5 empty] | 18.63
[11 empty] | 23.04.2026 | 11-12A dt. 28.04.2026 |  | 1: 7.2; 2: 32; 3: 128; 5: 46; 25: 300 |  |  |  | Non complying | Non complying |  | 7.1 | 126 | 312 |  | 248
[11 empty] | 12.05.2026 | 109-110A dt. 20.05.2026 |  | 1: 8.2; 2: 31; 3: 120; 5: 46; 11: ND; 25: 52000 |  |  |  | Non complying | Non complying |  | 8.9 | 141 | 496 |  | 352 | [5 empty] | ND | [13 empty] | 56000
[11 empty] | 10.06.2026 | 311-312A dt. 16.06.2026 |  | 1: 8.2; 2: 36; 3: 72; 5: 48; 11: 12.2; 25: 150 |  |  |  | Non complying | Non complying |  | 8.8 | 116 | 352 |  | 248 | [5 empty] | 32.4 | [13 empty] | 68000
[11 empty] | 06.07.2026 | 419-420A dt. 14.07.2026 |  | 1: 7.9; 2: 12; 3: 62; 5: 24; 11: 9; 25: 120; 52: BDL |  |  |  | Non complying | Non complying |  | 8.5 | 108 | 336 |  | 236 | [5 empty] | 28 | [13 empty] | 32000 | [26 empty] | 30
[11 empty] | 17.07.2026 | 515-516 dt. 30.07.2026 |  | 1: 9.4; 2: 46; 3: 164; 5: 38; 25: 2400; 52: 12 |  |  |  | Non complying | Non complying |  | 7.8 | 102 | 304 |  | 212 | [19 empty] | 42000 | [26 empty] | 36
[11 empty] | 03.08.2026 | 635 dt. 18.08.2026 |  | 1: 8.2; 2: 92; 3: 208; 5: 124; 25: 62000; 52: 32 |  |  |  | Non complying | Non complying
36 | (HSR-STP-009) 5 MLD STP Dhani Kushal , Bhiwani Road, Hansi , Hisar by PHED in 15.4.2014 |  | 30 | 5.5-9.0 | 250 | 50
[11 empty] | 28.01.2026 | 4377 dt. 09.02.2026 | 3.09 | 1: 7.29; 2: 7.8; 3: 48; 5: 16; 11: ND |  |  |  | Complying | Complying | 3.28 | 7.74 | 130 | 416 |  | 272 | [5 empty] | 15.22
[11 empty] | 03.02.2026 | 4426 dt. 16.02.2026 |  | 1: 7.01; 2: 7.6; 3: 40; 5: 13; 11: ND; 25: 50 |  |  |  | Complying | Complying |  | 7.59 | 105 | 360 |  | 180 | [5 empty] | 16.32
[11 empty] | 27.03.2026 | 4784 dt. 08.04.2026 | 4.4 | 1: 7.96; 2: 14; 3: 88; 5: 24; 11: 4.58; 25: 400 |  |  |  | Complying | Complying | 4.48 | 7.68 | 140 | 452 |  | 248 | [5 empty] | 20.78
[11 empty] | 28.04.2026 | 15-16A dt. 05.05.2026 |  | 1: 7.6; 2: 7; 3: 22; 5: 14; 25: 50 |  |  |  | Complying | Complying |  | 7.4 | 105 | 381 |  | 198
[11 empty] | 27.05.2026 | 220-221A dt. 04.06.2026 |  | 1: 7.9; 2: 9.2; 3: 48; 5: 19; 11: ND; 25: 96 |  |  |  | Complying | Complying |  | 8.4 | 140 | 504 |  | 232 | [5 empty] | ND | [13 empty] | 32000
[11 empty] | 10.06.2026 | 317-318A dt. 16.06.2026 |  | 1: 7.2; 2: 7.4; 3: 28; 5: 16; 11: 8.2; 25: 56 |  |  |  | Complying | Complying |  | 7.8 | 110 | 396 |  | 202 | [5 empty] | 28.2 | [13 empty] | 42000
[11 empty] | 01.07.2026 | 386-387-A dt.07.07.2026 |  | 1: 8.3; 2: 148; 3: 504; 5: 78; 25: 1.8X10⁴ |  |  |  | Non complying | Non complying |  | 8.2 | 265 | 664 |  | 316 | [19 empty] | 3.6X10⁴
[11 empty] | 16.07.2026 | 505-506 dt 30.07.2026 |  | 1: 8.5; 2: 28; 3: 76; 5: 38; 25: 1200; 52: 7 |  |  |  | Non complying | Non complying |  | 7.2 | 124 | 352 |  | 208 | [19 empty] | 39000 | [26 empty] | 42
[11 empty] | 04.08.2026 | 676-77 dt 11.08.2026 |  | 1: 7.2; 2: 14; 3: 112; 5: 48; 25: 360; 52: 6 |  |  |  | Non complying | Non complying |  | 8.6 | 96 | 192 |  | 196 | [19 empty] | 42000 | [26 empty] | 28
37 | (HSR-STP-010) 7.5 MLD STP Lalpura, Jind Road, Hansi , Hisar by PHED in 15.4.2014 |  | 30 | 5.5-9.0 | 250 | 50
[11 empty] | 28.01.2026 | 4378 dt. 09.02.2026 |  | 1: 7.96; 2: 85; 3: 304; 5: 1.7; 11: 14.24 |  |  |  | Non complying | Non complying
[11 empty] | 20.02.2026 | 4565 dt. 10.03.2026 |  | 1: 7.35; 2: 82; 3: 196; 5: 125; 11: 15.96; 25: 900 |  |  |  | Non complying | Non complying
[11 empty] | 27.03.2026 | 4787 dt. 08.04.2026 |  | 1: 8.08; 2: 24; 3: 96; 5: 36; 11: 3.89; 25: 70 |  |  |  | Non complying | Non complying |  | 7.65 | 150 | 496 |  | 208 | [5 empty] | 14.58
[11 empty] | 28.04.2026 | 17-18A dt. 05.05.2026 |  | 1: 7.3; 2: 29; 3: 62; 5: 96; 25: 860 |  |  |  | Non complying | Non complying |  | 7.4 | 116 | 473 |  | 284
[11 empty] | 18.05.2026 | 159-160A dt. 26.05.2026 |  | 1: 7.8; 2: 96; 3: 384; 5: 122; 11: ND; 25: 32000 |  |  |  | Non complying | Non complying |  | 8.7 | 140 | 464 |  | 256 | [5 empty] | ND | [13 empty] | 51000
[11 empty] | 10.06.2026 | 315-316A dt. 16.06.2026 |  | 1: 7.9; 2: 42; 3: 82; 5: 32; 11: 17.2; 25: 480 |  |  |  | Non complying | Non complying |  | 8.8 | 114 | 560 |  | 292 | [5 empty] | 36.4 | [13 empty] | 48000
[11 empty] | 01.07.2026 | 390-391-A dt.07.07.2026 |  | 1: 8; 2: 28; 3: 80; 5: 44; 25: 2.2 X10⁴ |  |  |  | Non complying | Non complying |  | 7.6 | 105 | 424 |  | 190 | [19 empty] | 5.6 X 10⁴
[11 empty] | 16.07.2026 | 507-508 dt. 30.07.2026 |  | 1: 8.6; 2: 24; 3: 80; 5: 49; 25: 4800; 52: 9 |  |  |  | Non complying | Non complying |  | 7.5 | 105 | 208 |  | 176 | [19 empty] | 62000 | [26 empty] | 34
[11 empty] | 04.08.2026 | 674-75 dt. 11.08.2026 |  | 1: 7.2; 2: 18; 3: 80; 5: 56; 25: 420; 52: 7 |  |  |  | Non complying | Non complying |  | 8.2 | 102 | 188 |  | 142 | [19 empty] | 48000 | [26 empty] | 24
Yamuna Nagar
38 | (YMN-STP-008) 2.5 MLD, Saraswati Nagar (Mustafabad) by PHED, Yamunanagar
Jan., 2025
[11 empty] | 25.02.2026 | 4587 dt. 10.03.2026 |  | 1: 7.68; 2: 5.8; 3: 36; 5: 11; 11: ND; 25: 60 |  |  |  | Complying | Complying
[11 empty] | 14.03.2026 | 4719 dt. 01.04.2026 |  | 1: 7.54; 2: 4.4; 3: 24; 5: 9; 11: ND; 25: 90 |  |  |  | Complying | Complying
[11 empty] | 10.04.2026 | 94 dt. 28.04.2026 |  | 1: 7.98; 2: 6.8; 3: 36; 5: 13; 11: ND; 25: 90 |  |  |  | Complying | Complying
May, 2026
[11 empty] | 16.06.2026 | 500 dt. 24.06.2026 |  | 1: 8.07; 2: 4.2; 3: 24; 5: 12; 11: 8.4; 25: 70 |  |  |  | Complying | Complying |  | 8.1 | 98 | 396 |  | 30 | [5 empty] | 21.01 | [13 empty] | 1.8X105
[11 empty] | 03.07.2026 | 585 dt. 10.07.2026 | 4434030.49 | 1: 7.24; 2: 6.4; 3: 40; 5: 13; 11: 1.92; 15: 0.73; 25: 70; 52: BDL(DL=02); 55: 732 |  |  |  | Complying | Complying | - | 6.98 | 100 | 332 |  | 172 | [5 empty] | 14.72 |  |  |  | 7.39 | [9 empty] | 1.24 X105 | [26 empty] | 32.5 |  |  | 1442